OPERATING CODE NO. 3

(OC3)

SYSTEM INCIDENTS REPORT

CONTENTS

(This contents page does not form part of the Grid Code)

Paragraph No/Title	Page Number

OC3.1   INTRODUCTION	2

OC3.2   OBJECTIVE	2

OC3.3   SCOPE	2

OC3.4   SYSTEM INCIDENTS REPORT	2

OC3.5   REPORTING ON FAULT EVENTS ………………………………………………………………….3

OC3.6   REPORTING ON LEARNING…………………………………………………………………………3

OC3.1	INTRODUCTION

OC3.1.1 	Operating Code No.3 ("OC3") is concerned with the monthly publication by The Company of an incident report and Frequency data for the National Electricity Transmission System.

OC3.2	OBJECTIVE

OC3.2.1	The objective of OC3 is for The Company to produce regular reports of incidents and frequency data. The reports and data are important to industry and the Grid Code Review Panel as they help monitor the effectiveness of the technical requirements in the Grid Code and Distribution Code.

OC3.3	SCOPE

OC3 applies to The Company.

OC3.4	SYSTEM INCIDENTS REPORT

OC3.4.1	The Company shall publish  weekly a report or dataset titled the System Incidents Report, which shall contain:

- a record of each and all of any of the following Events, defined as Significant Events, on

the National Electricity Transmission System:

- a loss of infeed or exfeed (import or export including generation, Demand and interconnection) of =>250MW;

- a Frequency excursion outside the limits 49.7-50.3Hz;

- a fault on the National Electricity Transmission System which:

A.    could be linked to the known or reported tripping of 250MW or more as reported in (i) above; and/or

B. (as detailed in section CC6.1.4) is linked to a change in the Transmission System voltage of:

I. 300kV or greater: > +/-5% for >15min; or

II. 132kV up to 300kV: > +/- 10% for >15min;

III. Voltage <0.85 PU for >= 1s

IV. Voltage > 1.1 PU for >=1 s

- any known demand disconnected >=50MW from the National Electricity Transmission System or other lesser demand if notified to The Company; and

- any Demand Control action taken;

- any recorded change in measured phase angle of 12 degrees or more in a time period =<20ms;

- any rate of change of Frequency exceeding 0.1Hz/s;

- any known super or sub synchronous oscillations between 0.1- 45Hz, with an amplitude of >=10mHz, a duration of >=10s, and a damping ratio of <3% for >=5s.

- a report of each such Significant Event including the following data in relation to each Significant Event as appropriate and available:

- the time(s) in hh.mm.ss.mmm of the Significant Event and any potentially related occurrences;

- any known or reported loss of Embedded Power Station(s) with locations and ratings where available or step increases in demand and GSPs indicating such losses;

- the Frequency record from at least seven different regions, including at least one record from within each Frequency Restoration Region, (in table and graphical format) at <=100 millisecond intervals for 30s before and a minimum time after the Significant Event where the minimum time is at least 30s, or until the frequency has recovered within 49.80 to 50.20 Hz, if longer;

- the Frequency (to 2 decimal places) immediately before the Significant Event;

- the Frequency (to 2 decimal places) immediately after the Significant Event;

- the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms over a sliding 100ms window;

- where known, the MW of all individual losses or trips related to the Significant Event;

- where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event using a defined nomenclature of BMU reference and other references as required;

- the location of any reported Transmission fault using substation references codes from the ETYS;

- the extent of any voltage dip associated with the Significant Event;

- an estimate of system inertia in MW.s at the time of the Significant Event showing discrete components of:

  - demand inertia, including as available embedded generation,

  - transmission connected generator inertia;

  - inertia services contracted by NESO, and

  - any other source of inertia.

and in addition, the amount of the system inertia provided by GBGF-I plant included in above ; and

- any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications;

- where available, the Dynamic System Monitoring and Power Quality Monitoring data from any plant that has tripped; and

- a report on known events and associated data (including event times hh.mm.ss.mmm) on the National Electricity Transmission System including:

- three phase faults;

- three phase to earth faults;

- phase to phase faults;

- phase to earth faults;

- the associated voltage dips – durations and spreads;

- over-voltages;

- under-voltages;

- voltage dips of >50%;

- lightning strikes

- Phase Jump Angle, >=12 degrees in <=20ms;

- Auto reclosure.

OC3.4.2	To obtain, manage, present, communicate and report the data in OC3.4.1 The Company shall:

(a)	present the System Incidents Report and provide, associated data in spreadsheet or other downloadable API data format;

(b)	maintain an area of the Website (including the Data-Portal) with a list of all historic System Incidents Reports and information on any process required for legitimate parties to obtain the reports (if reports are not available to download); and

(c)	notify all Electricity Distribution Licence holders and Network Operators at least weekly of every Significant Event and request information to fulfil its duties in OC3.4.1.

OC3.4.3	The Company shall prepare and publish the System Incidents Report weekly in accordance with the following timescales:

(a) a data cut-off date every seven days;

(b) data is to be collated, reviewed and processed

(c)   System Incidents Report to be published weekly, within 5 working days after the weekly cut-off date, where this period can be extended due to exceptional circumstances (such as bank holidays, storms, etc.) For the avoidance of doubt, if there are no incidents arising under OC3.4.1 (a)- (c) a System Incidents Report would, nevertheless, still be published stating that ‘No System Incident occurred in the reporting week’.

(d) where the System Incidents Report shows any two events which have occurred or could have occurred within 12s, NESO shall publish a bespoke report, titled  Enhanced System Incident Report on these events within 10 working days, which can be extended exceptional circumstances, and which shall include, if relevant and available:

(i) PMU data and analysis from nearby and remote substations,

(ii)  the Apparent Power interrupted in any network fault,

(iii) the locations and times (hh:mm:ss:mmm) of any fault detected, circuit breaker clearing, and reclosing, including any auto-reclose,

(iv) the Dynamic System Monitoring and Power Quality Monitoring from plant that tripped and other relevant plant,

(v) all other relevant data available to The Company, and

(vi) an analysis of the events including a probability analysis of the events being unrelated showing the likelihood of repetition in years.

OC3.4.4

  - The Company shall publish, in a spreadsheet or other downloadable API data format, continuous System Frequency data from at least seven different regions, including at least one measurement in each System Restoration Region, at a maximum of 100ms intervals,  (Historic Frequency Data), including the rolling  Electric Time error, and the cumulative duration of all frequency excursions outside the range 49.800 to 50.200 Hz and publish this hourly on the Website, no later than 1hour after the data was recorded.

OC3.4.5             The Company will use best endeavours to provide a report or reports (based on either the

historic reporting methodology, or on the Significant Incidents Reports methodology, or a mix of the two), on events for the period from 1 November 2017 until the first System Incidents Report pursuant to this Operating Code, such a report or reports to be made available within 4 months of implementation date of the modification.

OC3.5 	REPORTING ON FAULT EVENTS

OC.3.5.1 	The Company shall prepare and publish on the Website a report giving date, times (hh.mm.ss) that the fault was reported (noting this may be some seconds after the fault occurred) , location (with reference to ETYS substation codes), of actual three phase, three phase to earth, phase to phase and phase to earth fault events on the National Electricity Transmission System.  Information shall be published as soon as reasonably practicable following such an event.  For all faults appropriate 3 phase voltage waveform information will be provided if available.

OC3.6	REPORTING ON LEARNING

OC3.6.1            Where the analysis of events occurring on the National Electricity Transmission System as set out in OC3.5.1 gives rise to learning points which The Company believes are relevant to the industry, The Company will publish a report explaining the events, the analysis and information gained as applicable. The contents of the report will be anonymised to avoid identification of Users, connection sites and manufacturers of Plant and Apparatus except in circumstances where OC3.6.2 applies. Where information sourced from Users or manufacturers is included, permission will be sought before publication.

OC3.6.4	Using best endeavours, The Company shall produce an annual report at latest 1 month after the end of the 12-month reporting period, this Annual System Incidents Report shall:

- review and examine all the data in the previous 12 months of System Incidents Reports;

- compare trends to previous 12-month periods;

- highlight the most Significant Events and learnings from these;

- look for any trends or emerging issues for the System;

- publish analysis of frequency duration data and trends;

- provide updates on new or improved measurements and data collection and analysis on the System;

- request feedback from industry on analysis, learnings and trends.

The Company shall and present the Annual System Incidents Report to the Grid Code Review Panel and publish the report on the Website inviting comments for improvements and omissions which shall be considered and addressed in the following Annual System Incidents Report.

< END OF OPERATING CODE NO. 3 >

Definitions and house keeping to be added to mod.

8 instances with 6 terms:

- auto-reclose

- auto reclose

- Delayed Auto Reclose

- automatic reclosure

- auto reclosure

- auto-reclosures

Code Admin request to create definition and retrofit / correct all uses.