## Webinar 22.07.2026
# | Webinar Question | NESO Response
1 | What cost impact assessment has been done to support the decision to exclude DSOs or embedded generation to provide reactive power services? | Thanks for this question, as part of our response we think its important to account for the wider context of how embedded DER are managed/controlled via DNOs/DSOs. From a Voltage perspective there is a highly complex interaction between the Transmission System and the Distribution network configuration, along with use of automatic voltage tap changers. Furthermore, identified requirements on the transmission network are highly driven by how DNOs/DSOs manage their networks, ultimately resulting in MVAr spill onto the transmission network. Reactive power needs are highly locational and assets that are embedded within the distribution network are typically less effective at meeting Transmission-level needs. In addition, the effectiveness for such assets connected at the distribution level is complex, and can change as a result of the Distribution Network configuration at any time. NESO does not have direct access to this data, nor real-time visibility of it. The control room would require adequate visibility of each asset, along with the real-time configuration of the network in order to issue instructions and monitor performance. Ensuring that contracted DERs/services remain effective for the Transmission System, regardless of any changes made by the DNO, adds a significant additional layer of complexity. If we were to allow DER to participate in reactive power markets at this time, it would lead to the end consumer paying for an issue rather than addressing the network management issue on the Distribution Network at source through Codes and policy. Therefore, NESO strategy at this time is to focus on resolving issues through code and policy, in alignment with Ofgem's ED3 approach.
2 | Do we believe addressing this at the D network always is a whole system solution with lowest cost to end consumer? | Yes, when deciding on this approach with regards to DER participation we considered how this would fit into the wider whole system approach. We are pleased to see that Ofgem's ED3 decision aligns with our preferred option which accounts for both network levels.
3 | Seeing that the work to get to this decision has been going on for a while, when can stakeholders expect the next review of this decision? | The DER Strategy for Reactive Power Markets can be reconsidered in the future NESO's wider DNO Reactive Power Contribution Strategy is progressed and implemented, and the ED3 determinations take effect. The timeline for this will be context dependent. Any updates will be communicated via NESO's reactive power webpage.
4 | How does NESO plan to model and prevent "price loops" and counter-actions if a DSO clears its local reactive power market using a localized algorithmic objective that contradicts NESO’s transmission market clearing results? | NESO is working with the DSO teams to better align flexibility markets and to ensure efficient decisions are prioritised. As greater levels of flexibility are dispatched across the system this coordination will become increasingly important, including ensuring the correct data and information is available to all parties in a secure and timely fashion. In April we launched a data exchange solution enabling DNOs to indicate where a NESO action could conflict with a DNO network requirement or action (such as a DNO instruction for reactive power reasons). We are already harnessing this information from DNOs in DFS, where we are able to exclude participants for particular events where that is in the whole system interest. We continue to work with the Market Facilitator and all DNOs on deployment of such coordination rules across our services.
5 | Are DERs still eligible to participate in the South West Summer 2026 Reactive tender? | NESO has not launched a tender for any SW Reactive Requirements in 2026 at this time. We have only run a consultation on identified SW Reactive Requirements to inform NESO's next steps. In the consultation we have been clear responses from transmission and distribution parties are allowed. Any information received from distribution-connected parties will be used to understand the electrical influence of the asset on the transmission system. Importantly, for any distribution level assets that respond, NESO would explore with the relevant DNO how best to access this capability. In other words, a commercial contract with NESO may not be appropriate and other arrangements with the DNO may be required.
6 | How will NESO incorporate the DSOs' localized voltage management capabilities into your transmission outage planning and network topology optimization? | NESO Outage Planning will continue to work with TOs and DNOs to co-ordinate and optimise outage plans, as we do today, taking all relevant aspects of the operation of the system into account.
7 | As embedded generation is now excluded from NESO reactive power markets, is the intention to restrict access to active power markets too? | In short, no. This update about DER participation in Reactive Power Markets is purely about NESO's Reactive Power Markets. It is noted that the technical limitations that exist with regards to voltage / reactive power services at the distribution level are not present in Frequency and Response services and therefore DER can still participate in those services. DER is eligible to participate in other markets (e.g. for the provision of Response and Reserve services, as well as the Electricity Restoration Service). For more information, please check our Balancing Services webpage. Generally, NESO are focused on demand side flexibility and enabling it to operate across NESO markets where this is appropriate.
8 | You have publicly released these slides which state DNOs have network management issues, given DNOs have not previously been mandated to manage reactive power, is this not irresponsible wording from NESO given the collaborative approach required to find a whole system solution to this problem? | For clarity, the published slides describe the scale of transmission network management undertaken by NESO and the factors that influence it, including MVAr spill from DNO network operation. We are not commenting on issues within DNO networks, which are outside NESO’s remit; rather, we are referring to observations at the interface between transmission and distribution networks. Our intention with this communication is to set out DER Eligibility with regards to NESO Reactive Power Markets and the rationale for it. The rationale for this decision ties into a wider whole system problem, which NESO is committed to resolving collaboratively, to identify a solution which is in the best interest for our consumers. We fully respect that ED3 will bring in new roles and responsibilities for the DNOs and DSOs and we are committed to supporting these bodies, alongside Ofgem, to find a solution which ensures system stability and lowest cost to our consumers.
9 | Many embedded DER run in non-unity power factor modes. How will NESO manage the reactive power impact of allowing DER to participate in real power markets? | This Q&A webinar was designed to help communicate the decision that has been made regarding DER Eligibility in NESO's Reactive Power Markets specifically and why. It does not change / comment on how reactive power is provided as a by-product when market providers participate in real power markets. We note that in real power markets, market participants are required to inform NESO of their available capacity in accordance with BM/Grid Code/REMIT obligations, taking account of any limitations due to power factor setpoints. For the avoidance of doubt this is in place today for embedded BM parties.
10 | Which industry stakeholders were consulted during the decision making process? | This decision is the result of a topic that was originally consulted on during the Reactive Power Market Design Innovation Project (facilitated by AFRY) which carried out various industry workshops. The findings of this market design project, learnings from other reactive power procurement events, and wider whole system strategy requirements were all considered to determine NESO's decision.
11 | Didn't the NESO/UKPN Power Potential innovation project prove that DER were effective in addressing reactive power/voltage issues on the Transmission boundary? Can you please clarify how the outcomes from that have been considered in reaching this decision? | Following our response to Q1 (above), while DER could provide value at transmission level (to the extent of their effectiveness), it is important to consider the base system design and operational needs to enable this. We have determined that exploring DER/DSO participation in Reactive Power Markets has a key dependency on realising our proposed enduring reactive power management criteria as part of ED3, which includes introducing reactive power envelopes to GSPs with target power factors. We recently shared our proposal with DNOs and Ofgem for transparency ahead of the ED3 working groups. It's important to note that our position is not about defining how the criteria will be met (e.g. a build solution), but more defining the whole system need to ensure security, optimise consumer value, and enable exploration of future solutions / opportunities, such as DER/DSO reactive power market participation or others that may be identified. It is not a matter of conducting a CBA on a Distribution vs Transmission solution, its about defining the minimum requirements needed to ensure whole system operations are complementary by design and maximise system security as we progress towards net zero and CP30. Our position is driven by real world data, operational experience including lessons learnt from recent system blackouts in Europe and is complimentary to Ofgem's ED3 proposal. NESO look forward to discussing this further during the upcoming ED3 working group forums.
12 | What is the time frame for the DSO stepping in and implementing a new regime for distribution-connected solutions? | Timeframes are subject to Ofgem's determination. You can find their proposed timelines in Figure 2 in their ED3 Sector Specific Methodology Decision which was published on the 21st May 2026.
13 | Would NESO still expect BEGAs to provide ORPS from embedded DER? | There are no changes to any ORPS obligations in the Grid Code as a result of this decision. This decision is specific to NESO's Reactive Power Markets and its associated eligibility criteria only, and our proposed next steps to resolve root cause issues (Mvar spill) with DNOs/DSOs from a whole system perspective. This will be considered where applicable as ED3 proposals mature and embedded DERs with BEGAs should monitor the ongoing ED3 discussions for any impacts of these proposals.