## Sheet1
Action number | Workgroup Raised | Owner | Action | Comment | Due by | Status | Workgroup Closed
1 | WG1 | JSC | Share the slides presented at Workgroup 1 with Workgroup members | Slides shared on 12 November | WG2 | Closed | WG2
2 | WG1 | FK and JSC | investigate reporting practices in other countries (Europe, US, etc.). | Presented at WG2 | WG2 | Closed | WG2
3 | WG1 | FK and AU | Review STC sections and Energy Data Task Force requirements for data sharing. | Electricity licensing (from October 2025) - Publications - Ofgem Public Register | WG2 | Closed | WG2
4 | WG1 | GW | Assess cost and workload implications for Transmission Owners (TOs) providing additional real time data. | Wording amended after WG6 | WG2 | Closed | WG6
5 | WG1 | FK and JSC | Check NESO data triage process against Energy Data Taskforce guidelines. | Presented at WG2 | WG2 | Closed | WG2
6 | WG1 | FK and GN | FK & JSC to provide ballpark estimate resource costs for weekly vs. monthly reporting and consider the Iberian blackout impact. GN to draft and share a benefits case | Presented at WG2 | WG2 | Closed | WG2
7 | WG1 | MB | Suggest thresholds for publishing larger incidents weekly and smaller ones monthly; NESO to consider if this mitigates workload concerns. | Shared at Workgroup 4 | WG2 | Closed | WG5
8 | WG1 | FK | Clarify what improvements are possible now, what would require more time, and how much better future data could be. | Presented at WG2 | WG2 | Closed | WG2
9 | WG2 | MD | Provide sources or a public version of the NESO data classification guidelines. | The NESO SME confirmed that there is no public source for their internal data guidelines, but they are available upon request and will share the presentation with the Workgroup. | WG3 | Closed | WG3
10 | WG2 | GW | Investigate whether TO data is published and where it can be accessed. | The NESO SME provided an update on whether Transmission Owner (TO) data can be published and where it could best be accessed. Noting practicality and constraints around sharing PMU (Phasor Measurement Unit) data more widely and in real time. | WG3 | Closed | WG3
11 | WG2 | AL | Prepare a short presentation on phase jumps. |  | WG3 | Closed | WG3
12 | WG2 | JR and LT | Review the GC0181 defect description to determine if phase jump data can be included. |  | WG3 | Closed | WG3
13 | WG2 | JSC | Confirm the timing for when 73 PMUs (or at least 5) will be operational and consider regional coverage. | The NESO SME advised the Workgroup that NGET are considering timelines for the full PMU rollout, noting that Scotland's rollout is complete, and other regions are expected to follow, with significant progress anticipated by March 2026 and completion targeted by the end of 2027. They also mentioned that the same timeline applies to frequency, inertia and system resolution data and by December 2027, there should be sufficient rollout to access the necessary data. | WG3 | Closed | WG3
14 | WG2 | FK | Propose amended draft Legal text for the solution. | Legal text presented in WG3. | WG3 | Closed | WG3
15 | WG2 | FK and JSC | Confirm GB alignment with the European standard of 0.5 seconds for frequency recording. | GB currently aligns with European requirements for frequency data resolution, which is set at one second for frequency quality analysis, referencing Article 131.1A; the one-second resolution is used for frequency quality checks and event analysis, while frequency control in Europe uses lower resolutions (one minute and fifteen minutes); there is no ROCOF (rate of change of frequency) reporting requirement in the referenced European standards. | WG3 | Closed | WG3
16 | WG3 | MD | Provide the data guidelines and check if the direct policy documents can be shared with the Workgroup. |  | WG4 | Closed | WG4
17 | WG3 | FK | Provide more information regarding confidentiality, costs, and data sharing with the TOs. |  | WG4 | Closed | WG4
18 | WG3 | JAK | Provide information on PMUs being installed are of the same technology or specification and to clarify their technical capabilities. |  | WG4 | Closed | WG4
19 | WG3 | GN | Review and improve the framing of the cost-benefit analysis for blackout prevention, specifically by comparing the expected probability of a blackout event to the calculated benefit of enhanced reporting. |  | WG4 | Closed | WG4
20 | WG3 | MC | Provide specific information on the system incident report spreadsheet such as format changes. | Shared at Workgroup 4 | WG4 | Closed | WG4
21 | WG3 | ALL | Review legal text when circulated with updated wording. | Shared at Workgroup 4 | WG5 | Closed | WG4
22 | WG3 | MD | Share the background of numbers and reporting times for the System Incident Report. | Shared at Workgroup 4 | WG4 | Closed | WG4
23 | WG3 | GW | Provide map showing where future and current PMUs are installed and the identification of zones/regions these PMUs fall into. |  | WG4 | Closed | WG4
24 | WG3 | FK/JAK/MD | Contact EU TSOs to look at the frequency data resolution and see if they do more than the legislative standard. |  | WG4 | Closed | WG4
25 | WG4 | JSC | Provide more detailed cost data from NESO to confirm whether the placeholder figure of £50,000 per annum for weekly reporting is sensible |  | WG5 | Closed | WG5
26 | WG4 | JSC | Provide an example of a previous incident with attached PMU data to demonstrate how PMU data could be used in system incident reporting, once operational PMU data is available. |  | WG5 | Closed | WG5
27 | WG4 | JSC | Update the incident reporting tables for weekly and monthly incidents to include a complete record from 2022 to 2025, using available public data. |  | WG5 | Closed | WG5
28 | WG4 | MD | Create a process flowchart for the incident reporting process and a Gantt chart clarifying the steps and time allocations, including separation of working and waiting times. |  | WG5 | Closed | WG6
29 | WG4 | MD | Explore whether there is a record of the total number of events initially investigated each month and obtain this data if possible. |  | WG5 | Closed | WG6
30 | WG4 | AG | Consult with SMEs to clarify how phase jump angles, which are location specific, should be handled and reported in the legal text. |  | WG5 | Closed | WG5
31 | WG4 | FK/JSC | Define the degree or extent of the phase jump angle that qualifies as a significant event for inclusion in the legal text. | Phase jump angle as the 12-degree threshold has been included in the draft legal text. | WG7 | Closed | WG7
32 | WG4 | AG | Check whether auto-reclosures are reported in GC0151 and establish the teams and tools responsible for capturing this information |  | WG5 | Closed | WG6
33 | WG5 | FK/JSC | Investigate and propose language or process changes to decouple the reporting period from the report production timeline, including automation opportunities, to enable more timely system incident reporting. |  | WG6 | Closed | WG6
34 | WG5 | FK | Review and update references to PMU standards in relevant documents, ensuring alignment with the latest IEEE 2018 standard and STCP 2701 Appendix B, and recommend any necessary changes. Written summary still required. | NESO confirmed that a review of IEEE PMU standards had been undertaken, identifying that PMUs across GB operate to a mix of 2005, 2011, 2014 and 2018 versions, with the 2014/2018 standards broadly aligned. The action remains open, with a commitment to provide a written summary and clarify implications for compliance and any required updates to related documents. | WG7 | Open
35 | WG5 | FK | Align GC0181 data requirements with STCP 2701 Appendix B and clarify if a modification to the STC is needed to codify information exchange from TOs to NESO and NESO out. Written confirmation of the present view required. | NESO confirmed that work is ongoing to align STCP Appendix B data requirements with the proposed legal text and assessing how data would be shared with NESO. The action remains open, pending further clarity on the final legal text and any associated cross-code impacts. | WG7 | Open
36 | WG5 | FK/JSC | Map current and planned PMU locations to restoration regions and provide a clear visual representation, including coverage of HVDC links and bootstraps, to ensure comprehensive system monitoring. | NESO presented an initial view of current and planned HVDC links and PMU locations via mapping material, noting limitations in visualising all locations. The action remains open, with agreement to provide an updated approach using an itemised list of PMU locations alongside revised mapping. | WG7 | Open
37 | WG5 | JSC | Research and provide an update on the availability and inclusion of time error data in system incident reports, referencing its operational importance. |  | WG6 | Closed | WG6
38 | WG5 | FK | Contact EU TSOs to obtain information on any planned improvements to frequency data reporting and update the work group on future enhancements. | NESO shared findings from discussions with European TSOs, noting disparities in data reporting and sampling rates, and confirmed that the action on comparative learning could be closed. | WG7 | Closed | WG7
39 | WG5 | JSC | Confirm whether the OTF question regarding the correlation between double circuit faults and HVDC trips was addressed in today's OTF and share the findings with the Work group. | Update provided at WG7 | WG7 | Closed | WG7
40 | WG5 | FK | Share the NESO edited legal text with the Proposer for review | NESO confirmed that an alternative version of the legal text had been developed and shared with the Workgroup following the previous meeting. | WG7 | Closed | WG7
41 | WG5 | AL | Provide written guidance on phase jump angle reporting, including a proposed significance threshold (12°) and supporting rationale to inform legal text | The Proposer confirmed that written guidance on phase angle reporting and associated thresholds had been provided to the Workgroup. It was agreed this material should be published alongside the modification as an Annex to the Workgroup Consultation. | WG7 | Closed | WG7
42 | WG6 | SMc | Review precendent for asset renaming in GC0139 | NESO provided initial input on asset naming, noting that existing approaches rely on general principles of unique and persistent identifiers, with inconsistencies often resolved through bilateral clarification. The Workgroup agreed further work is required to establish consistent naming conventions across BMUs, GSPs, and transmission circuits. The action was closed but combined with Action 44 to create a new consolidated Action 50. | WG7 | Closed | WG7
43 | WG6 | SMc | Review terminology for online data portals and system restoration regions | NESO confirmed that the correct terminology for “system restoration regions” has been identified, however further clarification is required on how data should be made available (e.g. via data portal or API) within the legal text. The action remains open and will be addressed as part of the ongoing legal text review. Review terminology for online data portals and system restoration regions, including clarification of how data should be made available (e.g. via data portal or API) within the Legal Text. | WG7 | Open
44 | WG6 | SMC | Investigate existing standards for asset referencing | NESO confirmed that BMU and related asset naming is sourced from the Single Markets Platform, where participants register units and are assigned NESO BMU IDs. The Workgroup agreed this should be considered alongside Action 42, with further work required to establish a single, consistent naming standard; the action was closed but combined with Action 42 to create a new consolidated Action 50. | WG7 | Closed | WG7
46 | WG6 | GN | Refine legal text | A refined version of the Proposer’s legal text has been developed and circulated to the Workgroup. | WG7 | Closed | WG7
47 | WG6 | SMc | Explore feasibility of defining “auto‑reclosure". | NESO have reviewed the use of the term “auto reclosure” and identified varying terminology across the Grid Code. While recognising the benefit of standardisation, it was noted that changes would likely require a separate modification due to potential materiality; this will be explored further, with any follow-up via a separate modification. | WG7 | Closed | WG7
48 | WG6 | GN | Propose “exceptional event” flexibility in timelines | The proposer confirmed that requirements relating to exceptional event flexibility have been incorporated into the draft legal text. | WG7 | Closed | WG7
49 | WG6 | GN | Define the specific data requirements and reporting activities proposed under GC0181, in order to enable Transmission Owners to assess the cost and resource implications of implementing the proposal | The Workgroup discussed potential impacts on Transmission Owners and concluded that no significant additional requirements are currently anticipated, noting that much of the required infrastructure is already being developed through PMU rollout. The action was agreed as closed and replaced with a new action for NESO to present a high-level solution architecture to support understanding of delivery and implementation. | WG7 | Closed | WG7
50 | WG7 | SMC | Provide a single, consistent source/list for BMU, GSP, and transmission circuit names. |  | WG8 | Open
51 | WG7 | SMC/JSC | Develop and share a high-level architecture diagram showing information flow from PMU rollout to NESO systems. |  | WG8 | Open
52 | WG7 | JSC | Provide data on occurrences of voltage excursions below 0.85 and above 1.1 per unit for more than one second, to validate proposed reporting thresholds. |  | WG8 | Open
53 | WG8 | JSC | Following the provision of data from action 52, NESO to consider alternative voltage excursion thresholds and provide feedback to the Workgroup. |  | WG9 | Open
54 | WG9 | KK | Restructure and issue a revised draft of the Workgroup Consultation, incorporating the feedback and draft Workgroup Consultation questions from Workgroup Meeting 9. |  | WG10 | Open
55 | WG9 | GN | Update and provide the Proposer's draft Legal Text following Workgroup feedback. |  | WG10 | Open
56 | WG9 | KB | Prepare and submit the potential Alternative Request and supporting material for circulation before Workgroup Meeting 10. |  | WG10 | Open
57 | WG9 | AL | Provide high-level bullet points on the proposed order and justification for the executive summary for Code Administrator consideration. |  | WG10 | Open
58 | WG9 | KK | Prepare a revised modification timetable with the Proposer for Grid Code Review Panel approval. |  | WG10 | Open
59
60
61
62
63
64
65
66
67