| Workgroup Consultation |  |  |  |
| --- | --- | --- | --- |
| GC0181: Enhance the Effectiveness of System Incidents Reporting Overview: Reports are available for industry and the Grid Code Review Panel to monitor the effectiveness of technical requirements in the Grid Code and Distribution Code – resulting from GC0105 and GC0151 System Performance Reports. The data and the reports are not effectively serving their purpose due to the way the system incidents are being reported. This modification aims to be a further improvement of GC0105. |  | Modification process & timetable Proposal Form 12 August 2025 Proposal Form 12 August 2025 Workgroup Consultation 05 January 2026 - 26 January 2026 Workgroup Report 18 March 2026 Code Administrator Consultation 01 April 2026 - 01 May 2026 Draft Final Modification Report 17 June 2026 Final Modification Report 07 July 2026 Implementation 10 Business days after Authority decision 1 2 3 4 5 6 7 Workgroup Consultation 05 January 2026 - 26 January 2026 Workgroup Report 18 March 2026 Code Administrator Consultation 01 April 2026 - 01 May 2026 Draft Final Modification Report 17 June 2026 Final Modification Report 07 July 2026 Implementation 10 Business days after Authority decision 1 2 3 4 5 6 7 |  |
| Have 5 minutes? Read our Executive summary Have 60 minutes? Read the full Workgroup Consultation Have 120 minutes? Read the full Workgroup Consultation and Annexes. |  |  |  |
| Status summary: The Workgroup are seeking your views on the work completed to date to form the final solution to the issue raised. |  |  |  |
| This modification is expected to have a: Low impact on Transmission System Owners |  |  |  |
| Modification drivers: System Operability, System Security, Transparency |  |  |  |
| Governance route | Standard Governance modification with assessment by a Workgroup |  |  |
| Who can I talk to about the change? | Proposer: Guy Nicholson, Statkraft guy.nicholson@statkraft.com |  | Code Administrator Chair: Keren Kelly |
| How do I respond? | Send your response proforma to grid.code@neso.energy by 5pm on XX Month Year |  |  |

Contents

Executive Summary	3

What is the issue?	4

What is the defect the Proposer believes this modification will  address?	4

Why change?	4

What is the solution?	4

Proposer’s Original solution	4

Workgroup considerations	4

Alternative Requests	5

Workgroup Alternative 1 solution	7

Workgroup Alternative 2 solution	7

What is the impact of this change?	8

Original and Workgroup Alternative Proposer’s assessment against Code Objectives	8

When will this change take place?	8

Interactions	9

How to respond	9

Acronyms, key terms and reference material	10

Annexes	11

# Executive Summary

GC0181 proposes changes to the Grid Code to improve availability of data for analysis of system events where aspects of the system state exceed normal operational limits, but may still be within statutory limits. The improved availability of data aims to reduce the risk of system cascade event incidents, such as that which occurred in 2019.

The Modification builds upon previous Grid Code Modifications GC0105 ‘System Incidents Reporting’ and GC0151 ‘ Grid Code Compliance with Fault Ride Through Requirements’ which have key interactions with the Security and Quality of Supply Standard (SQSS) and Frequency Risk and Control Report (FRCR).

What is the issue?

The proposer considers the current System Incident Reporting process ineffective because incident reports are published too long after events occur and not frequently enough. Both the temporal and spatial resolution of data is not considered sufficient to support detailed analysis of system incidents. Additionally, the proposer believes the lack of clearly defined naming conventions included within the current reporting prevents automated analysis. As a result, industry parties are unable to investigate disturbances promptly or accurately, limiting understanding of the causes of system events and reducing the value of the reports for monitoring system performance and stability.

What is the solution and when will it come into effect?

Proposer’s solution: To be updated to reflect Proposer’s solution refined through Workgroup

Implementation date: 10 Business days after Authority decision

Summary of potential alternative solution(s) and implementation date(s):

Summary of any alternatives that have been discussed/raised (1-3 sentences).

What is the impact if this change is made?

The proposer believes the modification will have a positive impact on system operability, security, and transparency by enabling more timely and detailed analysis of system incidents, helping industry parties better understand trends in system stability and identify potential risks. The proposal is expected to improve the safety and reliability of the electricity system and deliver wider societal benefits through a more secure and resilient grid.

Interactions

Identify any interactions with other modifications, other codes/standards or other industry-wide work i.e. BSUoS Taskforce/Open Networks. (1-2 sentences)

[this should be no longer than one page]

What is the issue?

## What is the defect the Proposer believes this modification will  address?

The existing reporting process has three defects that need to be resolved to allow efficient and effective analysis of incidents/trips. The defects include late reporting of incidents with insufficiently low data sampling rate and lack of regional data from the place of incident. Due to these defects, the industry and relevant parties are unable to carry out effective analysis in a timely manner which further prevents understanding the cause of Grid disturbance events.

The existing reporting process has room for improvement to increase its effectiveness.

Here are some key areas the Proposer believes need improvement:

- Reports are made available to the industry quite late, often three months after the events have occurred.

- In the Proposer view, the data sampling rate is insufficient for thorough analysis.

## Reports do not incorporate data from various locations across Great Britain (GB).

# Why change?

- This situation hinders timely analysis, and the lack of information leads to doubt and confusion regarding the background of the incident. The Iberian blackout serves as a prime example of the consequences of not having timely data. When the Iberian blackout happened on 28 April 2025, industry, society and other bodies wanted to know the details of the incident the day after its occurrence and not three months later. Since the data is published long after the event, it becomes less useful, as industry are not receiving up-to-date information.

Moreover, the additional data that Users may have from their sites that would support the investigation of the incident, is not stored indefinitely as it requires a lot of storage. Thus, this data is less likely to be available. Hence, the sooner the industry gets to know about an incident, the easier it is to find the data from the sites and investigate it. Referring again to the Iberian blackout, when industry see the reports, it is easy to see that there was a voltage control problem.  If this data had been published before the event, then there is a good chance that these issues would have been spotted and corrected before a blackout.  The same principle applies here to GC0105 ‘System Incidents Reporting’ and GC0181. On 22 December 2023, an event occurred where one of the interconnectors between France and the UK (IFA2) tripped, causing a 49.2Hz frequency event and leading to a loss of 2GW on the UK grid and NESO was able to publish the incident data on 17 January 2024, during the Operational Transparency Forum.

This happened in less than a month's time, despite the Christmas and New Year holiday period. This demonstrates that NESO can release data in under a month. If they were routinely publishing data, they should be well-equipped to do so.

- The frequency data that the Users are receiving is not accurate enough. 
The sampling rate of the frequency data published by NESO on the System Performance Reports is 1 second which is very low. For the 22 December 2023 event, the Proposer has done a Rate of Change of Frequency (RoCoF) calculations in two ways as can be seen below:

Using the first method that is based on MW loss and inertia, the RoCoF of Interconnector trip is -0.155Hz/s and using the second method based on frequency measurements, the RoCoF is -0.102 Hz/s. So, the method 1 value is 52% higher than method 2 value. In the same manner, for the Cottam Development Centre Limited (CDCL) unit trip, the method 1 value is 33% higher than the method 2 value. Therefore, there is an average of ~40% error in RoCoF value from frequency measurements versus RoCoF based on MW loss and inertia.

If more granular frequency could have been used, the RoCoF values calculated using the two methods above would have been much closer and the error being much less. Hence, a shorter sampling period is required to get more accurate RoCoF. With the current sampling rate of 1 second, the frequency data is too averaged so it's masking the real RoCoF. Moreover, if accurate frequency data is not available, then the loss cannot be calculated properly as it was needed for the High Voltage Direct Current (HVDC) link trip during the 22 December 2023 event. There was no knowledge of what was lost in the HVDC link trip so inertia data could not be used either to calculate the loss. Hence, the data had to be interpolated to find out the loss as shown below:

Thus, it shows the kind of errors that can occur when industry don’t have the right data.

- It is important because some areas might experience RoCoF values significantly higher than the national average. The frequency in a Synchronous Grid is generally treated as a parameter consistent across the entire system. However, over short durations, phase differences throughout the Grid can cause minor variations in the actual frequency at different points. This results in differing rate of RoCoF across the network which can be found in the Project Resilient Electric Vehicle Charging “REV” Report, for reference. Moreover, the Spanish investigations into the Iberian blackout show that there are regional variations and oscillations in frequency which can be found in the ENTSOE Iberian blackout report. This further proves the need and significance of regional data in analysing incidents.

The Original Proposal form can be found in Annex 01.

What is the solution?

## Proposer’s Original solution

NESO should analyse the data and publish an annual report to track trends in system stability compared to previous years. This is essential for monitoring any adverse trends in system stability. The report should contain generic analysis that is done by aggregating the data of all the incidents that have occurred in that year. The analysis should be done in several categories including:

- analysis done against the time of the day,

- analysis done against the days of the week,

- analysis done on a quarterly basis,

- the type of Balancing Mechanism Units (BMU) responsible for causing each trips/incidents,

- the extent of the trips such as the total number of trips caused by the BMUs,

- the total MW loss associated with the trips; and

- the average loss (MW) per event.

The Proposer recommends the following requirements for NESO in its capacity as the GB System Operator in the Grid Code Operating Code (OC)3.4:

- OC3.4.3 - Reduce the reporting time from the current three months to one week.

- OC3.4.1(b)(iii) - Increase the sampling rate from the existing 1 second to 100 milliseconds.

- Gather frequency measurements from at least five different regions across Great Britain.

Additionally, the Proposer is keen to receive feedback from the Workgroup regarding other potential improvements and solutions.

## Proposer’s Updated Solution

The initial proposal was formally presented to the members of the Workgroup during the first Workgroup meeting on 04 November 2025. Subsequent to comprehensive discussions within the Workgroup, the Proposer refined their Original solution, resulting in the updated version outlined below:

Further update/check required to ensure this section reflects the proposer’s solution refined through Workgroup

## Draft legal text

The draft legal text can be found in Annex 03.

Workgroup Consultation question X: Xxxxx?

Workgroup considerations

The Workgroup convened XX times to discuss the issue as identified by the Proposer within the scope of the defect, develop potential solutions, and evaluate the proposal in relation to the Applicable Code Objectives.

Workgroup Discussion ahead of the Workgroup Consultation

NESO’s Current System Incident Report process

Include link to current System Incident Reporting

NESO presented a confidential task breakdown for producing frequency reports, covering data extraction, running analytical code, investigation, requesting information from TOs, and final review.

The NESO SME outlined:

- the frequency incident reporting process, estimating Full Time Employees (FTEs) days for monthly and weekly reports under normal and stormy conditions;

- event investigation volume drives workload, weekly reports may require similar effort as monthly ones;

- monthly reports take 13.3 FTE days, weekly reports 11.5 FTE days and extra FTEs help but don't halve the time due to process bottlenecks;

- PMU data use reduces reporting time, and weekly reports could be 8 FTE days, or 3.6 with an extra FTE;

- reporting depends on IT systems, holidays, control room support and region count.  More regions mean more time;

- some event data is already published externally.  The benefit of more frequent reporting for blackout prevention is questioned. Bi-weekly reporting is suggested as a practical compromise.

Workgroup members discussed how reportable events are identified; NESO described checks across BMU outputs, control room reports, REMIT, Elexon, and other sources to confirm Grid Code criteria are met.

A Workgroup member explained that when using the System Incident Report spreadsheet, their team converts data to absolute figures and finds some columns irrelevant for their analysis, though they may be useful to others.  They requested that the generation source be added to the spreadsheet, as this is currently a manual process for their team.  The NESO SME invited the Workgroup members to share specific feedback on the spreadsheet format changes that would help team, e.g. adding the generation source and clarifying which columns are relevant.

NESO agreed to produce a process flow chart; check whether records exist showing the total number of events initially analysed each month; and update incident reporting tables for completeness. NESO SME also noted a need to improve messaging and clarify dependencies in future discussions.

NESO raised feasibility concerns for some data requirements (e.g., 100 ms frequency data and phase jump angles), given tool limitations and data volumes. Some requirements remain open pending further NESO review and tool development, with actions to clarify technical capabilities.

Cost Benefit Analysis (CBA)

The Proposer presented an impact assessment comparing the cost of the Iberian blackout to potential costs in GB. Estimating a GB blackout could cost around £13 billion, with the benefit of improved reporting, moving from monthly to weekly, far outweighing the operational cost.

The analysis showed that if enhanced reporting prevented even one blackout every 260,000 years, it would be cost-effective.

The main Workgroup discussions were:

- whether the information required by OC 3.4, related to GC105, could prevent a blackout, noting the benefit depends on whether the reporting can truly stop such events.  The Proposer clarified that the goal is not to guarantee blackout prevention, but to reduce the probability by increasing transparency, analysis, and pre-emptive action.  Past improvements in protection settings like RoCoF and vector shift relays which are examples of how better information has helped avoid system issues;

- that reporting alone cannot stop a blackout, but it does provide valuable transparency and system visibility, which can help identify risks earlier;

- suggestions of reframing the CBA to compare the expected probability of a blackout based on security standards to the calculated benefit, to better contextualise the value of improved reporting.  The Proposer agreed to review and improve the framing of the cost-benefit analysis for blackout prevention, specifically by comparing the expected probability of a blackout event to the calculated benefit of enhanced reporting

- clarification was needed on how producing a weekly report, as opposed to a monthly report, would make a difference in preventing a blackout, expressing uncertainty about the practical impact of increased reporting frequency on blackout prevention.

- The Proposer used a placeholder of £50,000 per annum for weekly reporting in the CBA, seeking confirmation from NESO. A Workgroup member indicated that weekly data provision should not be cost prohibitive, but more detailed breakdowns are needed for accuracy.

NESO Impact

NESO presented its view on the costs and benefits of moving to weekly reporting, highlighting the increased workload, requirement for process changes, significant expansion of data storage capability, while also potentially resulting in empty reports during weeks with few or no events.

Several Workgroup members questioned the magnitude of the cost increase, arguing that much of the data processing is already being done and that the main change is in the frequency of publication, not the underlying analysis and reiterated that publishing data leads to greater system efficiency, consumer benefit, and innovation, referencing the Energy Data Task Force's findings and Ofgem's call for improved data transparency.

The NESO representative further clarified that the number of incidents formally reported is significantly lower than the total number of events actually analysed. The reporting process requires thorough sifting and extensive cross-referencing (which includes control room reports, among other data sources) to ensure accuracy and compliance.

The main bottleneck is waiting for TO data. Timelines are also affected by operational conditions, tool reliability, and staff availability.

NESO assessed using PMU data and additional FTEs to accelerate reporting, but noted that dependencies on other teams and end to end information flows limit the benefit of staffing increases alone.

Under best case assumptions, PMUs available and favourable conditions, NESO estimated the reporting period could reduce to 3.38 days; however, a weekly reporting cadence remains challenging and may not be feasible.

NESO expressed that considering all the blockers and challenges, the only feasible reporting frequency is monthly with a one-month reporting window. The main blockers to achieve a weekly report delivery are data collection including third party data request (DFR and PMU), data validation, data analysis, peer-review and approval. In addition to the main blockers, other challenges impacting the reporting delivery include bank holiday tightening the publication deadlines, IT issues, resource allocation to support the control room during emergency system operation conditions.

A Workgroup Observer noted that NESO demonstrate via data portal that weekly or more frequency reporting is possible via automated system. Only if specific concerns arise regarding data quality these can be highlighted and addressed after data has been published for a while. For example System Inertia | National Energy System Operator notes on the webpage NOTE: Updates to the System Inertia dataset have been temporarily paused while we review and validate the most appropriate data available.

Reporting cadence options were discussed, the NESO SME stated monthly is currently feasible; the Proposer and another Workgroup member suggested transitional steps (e.g., fortnightly), or moving to weekly once PMU data is operational. The Workgroup agreed to revisit this after further analysis and tool implementation.

Workgroup members strongly agreed with the Proposer on the importance of timely incident reporting for pre-empting blackouts and identifying system trends.

The Workgroup discussed that the current three month reporting lag and unhelpful data formatting make it difficult to analyse incidents and update their own reports promptly.  Suggestions of more frequent bi-weekly reports would provide a clearer, up to date picture of system events, enabling earlier trend identification and better industry preparedness

A Workgroup member asked whether NESO could use licence condition D2 to require TOs to provide information within set timelines, suggesting this could be formalised in the System Operator Transmission Owner Code (STC) to streamline data provision for incident reporting.  The NESO SME responded that while Phasor Measurement Unit (PMU) rollout will eventually provide live data, current processes still rely on manual requests.  The need for a code modification or further discussion may diminish as PMU coverage improves.

One Workgroup member suggested having thresholds for publishing larger incidents and smaller incidents monthly.  The NESO SME responded that NESO reviewed the idea of publishing larger incidents more frequently and smaller ones monthly but noted that defining thresholds for "larger" and "smaller" incidents needs official clarification, especially as the 250MW threshold is under review due to system dynamics.

The Workgroup discussed automating the reporting process could be improved by using RoCoF thresholds instead of just MW loss, which might make it easier to automate incident detection and reporting.  Noting that that the current 250MW threshold is intended to capture the required events and switching to a RoCoF based threshold could complicate things and would need further thought.  It was emphasised that, despite the potential for PMU data to reduce reporting time, many events near the lower MW threshold still require manual investigation.  This is due to false positives and the difficulty of automating the identification of all relevant incidents.

The Workgroup agreed to continue considering whether changes to the code could support greater automation, with the Proposer encouraging the NESO SME to explore options that would maintain data quality while making the process more efficient.

Cost and Feasibility of System Incident Reporting

NESO SME provided an overview of the organisation’s current data capabilities, highlighting limitations related to data granularity and confidentiality. The Workgroup subsequently considered the feasibility of implementing weekly reporting, increased sampling rates, and the inclusion of regional data, noting concerns regarding resource requirements and data ownership. The operational challenges posed by the proposal, particularly the need for high-resolution data and additional resources were highlighted.

NESO SME estimated that preparing the report would require one additional full-time employee, with an annual cost between £180,000 and £200,000. However, the SME stressed that factors such as limited data availability, the need to prioritise resources during incidents, and the requirement for complete data from TOs make weekly reporting impractical. As a result, monthly reporting is considered the most reliable minimum frequency.

The Proposer recommended separating the timing of incident reporting from the timeline for publishing full reports. This approach would allow incidents to be flagged promptly, even if comprehensive reporting requires additional time. Meanwhile, other Workgroup members emphasised the importance of using adaptable language in the legal text to support ongoing process improvements and the integration of automation.

Workgroup members recommended enhancing automation for both data extraction and report preparation. NESO SMEs acknowledged that automating the extraction of PMU data is feasible; however, the process of analysing this information and combining it with fault recorder data still demands manual effort. This is particularly important when handling complex incidents, where human expertise is required to ensure accurate integration and interpretation.

Transmission Owner Impact

The Workgroup discussed potential impacts on Transmission Owners (TOs) and concluded that no significant additional requirements are currently anticipated, noting that much of the required infrastructure is already being developed through PMU rollout. NESO will present to the Workgroup a high-level solution architecture to support understanding of delivery and implementation following further solution development.

The Workgroup highlighted that incident reporting relies on TO provided data; delays may require escalation, potentially involving the STC Panel if changes are needed to formalise data-sharing obligations and/or timelines.

Process Flow, Event Filtering, and Reporting Logic

The NESO Representative presented Gantt charts that compared the current reporting process with an optimised, best case scenario. These charts demonstrated that the majority of tasks occur in sequence, and that adding more staff or increasing automation would only slightly shorten the overall timeline. This is primarily because much of the process depends on waiting for data from TOs, which introduces unavoidable delays.

The Proposer presented data illustrating the monthly and weekly distribution of incidents, noting that while weekly reporting may lead to an increased workload, the impact is not substantial.

NESO SME explained that thousands of potential events are initially flagged each month, narrowed down using macros and manual checks to a smaller set for detailed analysis, with only a subset ultimately reported; the Workgroup members requested clearer documentation of each filtering step and its alignment with Grid Code OC3.

Workgroup members noted the importance of including embedded generation loss and Distribution Network Operator (DNO) data in the process flow, with NESO SMEs agreeing to update the Gantt chart to reflect these steps and improve transparency.

Proposed New or Amended System Incidents Report Requirements

The following section sets out the proposed amendments to requirements in OC3 with associated rationale and Workgroup discussion.

Record of Significant Events

- Reporting Frequency:

OC3.4.1 The Company shall publish weekly a report or dataset titled the System Incidents Report, which shall contain:

- Voltage

OC3.4.1 (a)(iii) B III. Voltage <0.85 PU for >= 1s

OC3.4.1 (a)(iii) B IV. Voltage > 1.1 PU for >=1 s

- Phase Jump Angle

OC3.4.1 (a)(vi) any recorded change in measured phase angle of 12 degrees or more in a time period =<20ms;

NESO SME explained that, at present, phase jump angles are not actively monitored. However, monitoring capabilities will soon be available within the Wide Area Monitoring System (WAMS), allowing for configurable settings. Detection will focus on specific buses, and event-based thresholds will be used to minimise unnecessary or false reports.

The Proposer proposed treating phase jump angles ≥5° as significant events; NESO advised this requires further discussion in the grid-forming expert group, including clarification of measurement capability and location specific considerations.

A Workgroup member suggested starting with a 12-degree threshold based on historical data, while the Proposer emphasised the need for a pragmatic, best endeavours approach to reporting, adjusting thresholds as more data becomes available.

A Workgroup observer shared analysis which informed the inclusion of a 12-degree phase jump angle within 20 milliseconds as a trigger for System Incident Reports within the proposed legal text, with the Proposer and NESO SME debating the practicality and benefit of monitoring such events given current data limitations. Phase Jump Incident Reporting slides shared with the Workgroup can be found in Annex 06.

The NESO SME shared that NESO acknowledges that phase angle jumps are a relevant power system phenomenon and recognises the evidence presented regarding historical Vector Shift concerns, generator ride-through requirements, and the growing importance of phase angle behaviour as inverter-based resources (IBRs) increase on the system. However, NESO does not currently have the operational capability to monitor, assess and report phase jump events in the manner proposed. Although future Wide Area Monitoring System (WAMS) capabilities are expected to improve this, the platform is not yet operational and key aspects, including monitoring coverage, measurement accuracy, reporting functionality, monitored locations, data retention requirements and associated operational processes, have not yet been assessed. As a result, NESO is unable to determine the practical feasibility of implementing the requirement or estimate the number of reportable events that may arise.

NESO shared that they also consider that further evidence is required to justify the proposed reporting threshold of a 12-degree phase angle change within 20 ms. An explanation has been provided that the threshold represents a compromise between historical Vector Shift settings and international ride-through requirements, but they do not believe this demonstrates that these values are the most appropriate reporting criteria from a system operation perspective.

A Workgroup observer suggested that NESO could consider committing to an innovation project within the next twelve months to establish suitable monitoring and reporting capabilities, identify appropriate monitoring locations and methodologies, validate the proposed thresholds, and assess the associated implementation, governance and reporting impacts.

The Workgroup agreed to use the Grid Code term 'phase jump angle' for consistency and discussed the need to align guidance documents and compliance requirements with formal Grid Code modifications.

- Rate of Change of Frequency/RoCoF:

OC3.4.1 (a)(vii) any rate of change of Frequency exceeding 0.1Hz/s;

- Frequency excursion:

- Super or sub synchronous oscillations

OC3.4.1(a) (viii) (v)any known super or sub synchronous oscillations between 0.1- 45Hz, with an amplitude of >=10mHz, a duration of >=10s, and a damping ratio of <3% for >=5s.

Data to be reported for each Significant Event:

- Millisecond requirement

OC3.4.1(b) (i) the time(s) in hh.mm.ss.mmm of the Significant Event and any potentially related occurrences;

- Embedded Power Stations

OC3.4.1(b) (ii) any known or reported loss of Embedded Power Station(s) with locations and ratings where available or step increases in demand and GSPs indicating such losses;

- Regional requirement

OC3.4.1(b) (iii) the Frequency record from at least seven different regions, including at least one record from within each Frequency Restoration Region, (in table and graphical format) at <=100 millisecond intervals for 30s before and a minimum time after the Significant Event where the minimum time is at least 30s, or until the frequency has recovered within 49.80 to 50.20 Hz, if longer;

The Workgroup reviewed the draft legal text and refined wording on regional PMU data requirements, "at least five different regions if available", and sampling rates. Consensus was to include flexibility for data availability and to further assess technical feasibility and costs. Key discussion points included whether clause OC3.4.1(b) should explicitly require multiple regions, whether frequency data should come from specific PMUs or be averaged across several to address data quality and confidentiality concerns, and whether a historical comparison test could show if averaging masks important deviations; a potential compromise was to refer to “representative” PMUs for defined areas rather than naming individual assets.

- Sliding window

OC3.4.1(b) (vi) the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms over a sliding 100ms window

- Standardised nomenclature

OC3.4.1(b) (viii) where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event using a defined nomenclature of BMU reference and other references as required;

NESO provided initial input on asset naming, noting that existing approaches rely on general principles of unique and persistent identifiers, with inconsistencies often resolved through bilateral clarification. NESO confirmed that BMU and related asset naming is sourced from the Single Markets Platform, where participants register units and are assigned NESO BMU IDs. The Workgroup agreed further work is required to establish consistent naming conventions across BMUs, GSPs, and transmission circuits.

- ETYS references

OC3.4.1(b) (ix) the location of any reported Transmission fault using substation references codes from the ETYS;

- Inertia

OC3.4.1(b) (xi) an estimate of system inertia in MWs at the time of the Significant Event showing discrete components of:

a.	demand inertia, including as available embedded generation,

b.	 transmission connected generator inertia;

c.	inertia services contracted by NESO, and

d.	any other source of inertia.

and in addition, the amount of the system inertia provided by GBGF-I plant included in above;

- Data from any plant that has tripped

OC3.4.1(b)(xiii) where available, the Dynamic System Monitoring and Power Quality Monitoring data from any plant that has tripped;

The Workgroup discussed the potential for enhanced monitoring using dynamic system monitoring platforms and remote access to generator data. The NESO SME described ongoing work to develop a platform for aggregating such data. Concerns were raised regarding commercial sensitivity of generator data, balanced against the benefits of shared learning and system reliability. It was argued that transparency should take precedence where it supports system security.

Detailed reporting on known events:

- Xxx

OC3.4.1 (c) a report on known events and associated data (including event times hh.mm.ss.mmm) on the National Electricity Transmission System including:

- three phase faults;

- three phase to earth faults;

- phase to phase faults;

- phase to earth faults;

- the associated voltage dips – durations and spreads;

- over-voltages;

- under-voltages;

- voltage dips of >50%;

- lightning strikes

- Phase Jump Angle, >=12 degrees in <=20ms;

- Auto reclosure.

The Proposer explained Section C as covering wider transmission faults/events beyond significant incidents. NESO noted that auto reclosures are not currently reported under GC0151 and GC0105 due to frequency and asset ownership. The NESO SME clarified that auto reclosure events are reported only when they are linked to detected fault currents. Incidents involving maloperations or equipment failures are excluded from reporting. The relevant data is gathered from TOs and carefully verified before being included in official reports.

Workgroup members advocated for more precise definitions of reportable faults, suggesting that voltage versus time profiles exceeding generator ride-through requirements should trigger reporting, to better address risks of cascading failures.

During the review of draft legal text, the Proposer suggested introducing a defined term for ‘auto-reclose’ or ‘auto reclosure’ into the Grid Code. NESO reviewed and fed back that they had identified varying terminology across the Grid Code. While recognising the benefit of standardisation, it was noted that changes would likely require a separate modification due to potential materiality, but this would be captured from a Code Administrator perspective with the opportunity to address in future.

Data Sharing:

- Mechanism for data sharing

OC3.4.2 To obtain, manage, present, communicate and report the data in OC3.4.1 The Company shall:

(a)	present the System Incidents Report and provide, associated data in spreadsheet or other downloadable API data format;

(b)	maintain an area of the Website (including the Data-Portal) with a list of all historic System Incidents Reports and information on any process required for legitimate parties to obtain the reports (if reports are not available to download); and

(c)	notify all Electricity Distribution Licence holders and Network Operators at least weekly of every Significant Event and request information to fulfil its duties in OC3.4.1.

The Workgroup discussed the terminology for data publication, debating the use of 'downloadable API' versus 'data portal' or 'downloadable data format,' and agreed to revisit the wording in the legal text as the proposed solution is developed. The Proposer clarified that the proposal does not mandate a specific report format and welcomed innovative approaches, such as searchable databases, to make the data more accessible and useful.

The Workgroup considered whether the solution should improve the existing reporting process or enable a more substantially automated process. A Workgroup member noted that real-time data processes existed elsewhere in industry and asked whether a redesigned process could be more effective than incremental efficiency changes. The Proposer referred to previous comments about automation and stated that the drafting was intended to allow reporting to begin and improve as automation developed.

- Timing of data sharing

OC3.4.3 The Company shall prepare and publish the System Incidents Report weekly in accordance with the following timescales:

(a) a data cut-off date every seven days;

(b) data is to be collated, reviewed and processed;

(c) System Incidents Report to be published weekly, within 5 working days after the weekly cut-off date, where this period can be extended due to exceptional circumstances (such as bank holidays, storms, etc.). For the avoidance of doubt, if there are no incidents arising under OC3.4.1 (a)- (c) a System Incidents Report would, nevertheless, still be published stating that ‘No System Incident occurred in month the reporting week’.

The Proposer noted the importance of distinguishing reporting frequency from publication delay. The proposed solution is seeking weekly reporting with publication five working days after the end of the relevant week, subject to flexibility for exceptional circumstances. The Workgroup also debated how to define “working days” to avoid deadline slippage around holidays and resource constraints, with an option to specify deadlines relative to weeks. Following Workgroup discussion, the Proposer included requirements relating to exceptional event flexibility.

Enhanced System Incident Report:

- Coincident events

OC3.4.3 (d) where the System Incidents Report shows any two events which have occurred or could have occurred within 12s, NESO shall publish a bespoke report, titled, Enhanced System Incident Report on these events within 10 working days, which can be extended exceptional circumstances, and which shall include, if relevant and available:

(i) PMU data and analysis from nearby and remote substations,

(ii)  the Apparent Power interrupted in any network fault,

(iii) the locations and times (hh:mm:ss:mmm) of any fault detected, circuit breaker clearing, and reclosing, including any auto-reclose,

(iv) the Dynamic System Monitoring and Power Quality Monitoring from plant that tripped and other relevant plant,

(v) all other relevant data available to The Company, and

(vi) an analysis of the events including a probability analysis of the events being unrelated showing the likelihood of repetition in years.

The Proposer presented findings from FOI responses concerning coincident events, including a double circuit fault (Coventry-Ratcliffe-on-Soar / Drakelow-Ratcliffe-on-Soar) and interconnector trip in November 2025. It was noted that precise timestamp data was not available at millisecond resolution, and that monitoring of phase jump angles was not active. Concerns were raised about inconsistent reporting practices, including the use of “representative time” instead of actual event time. The discussion highlighted uncertainty around whether events occurring in close temporal proximity were related, and the limitations of available data in determining causality.

The NESO SME clarified that the coincident events presented were determined to be unrelated based on investigations with relevant parties, despite occurring at the same second. One event was attributed to a transmission tower collapse associated with flooding, while the other was an Interconnexion France-Angleterre (IFA) trip due to an undisclosed issue on the French side, confirmed by National Grid Ventures, the counterparty for the IFA interconnector responsibilities on the GB side. Both events were determined to be unrelated after investigation using technical and operational evidence. The Proposer reiterated the need for probabilistic analysis of event coincidence, maintaining that understanding likelihood remains important even if events are deemed unrelated.

The full FOI responses can be found in Annex 04 and Annex 05.

System Frequency data publication

- Data publication at more frequent intervals

OC3.4.4 The Company shall publish, in a spreadsheet or other downloadable API data format, continuous System Frequency data from at least seven different regions, including at least one measurement in each System Restoration Region, at a maximum of 100ms intervals,  (Historic Frequency Data), including the rolling Electric Time error, and the cumulative duration of all frequency excursions outside the range 49.800 to 50.200 Hz and publish this hourly on the Website, no later than 1hour after the data was recorded.

A Workgroup member highlighted discrepancies between reported and actual electric time error data, stating that FOI results showed frequent exceedance of established limits set out in the Security and Quality of Supply Standards (SQSS). This raised broader concerns about data accuracy and consistency across reporting channels. The importance of reliable and transparent data was emphasised as a key driver for the modification.

Reporting on Fault Events

- Increased detail on fault events

OC3.5.1 The Company shall prepare and publish on the Website a report giving date, times (hh.mm.ss) that the fault was reported (noting this may be some seconds after the fault occurred), location (with reference to ETYS substation codes), of actual three phase, three phase to earth, phase to phase and phase to earth fault events on the National Electricity Transmission System.  Information shall be published as soon as reasonably practicable following such an event.  For all faults appropriate 3 phase voltage waveform information will be provided if available.

Timestamp accuracy and event sequencing

Workgroup members discussed challenges in obtaining precise timestamps from protection systems, noting reliance on data reception time rather than actual event occurrence. It was emphasised that accurate sequencing of events within seconds is critical to understanding cascading failures. A Workgroup member proposed leveraging PMUs and digital fault recorders to obtain high precision timestamps, reducing reliance on manual data retrieval. A new suggestion was raised to require generators to automatically provide fault recorder data following trips to improve post event analysis. The NESO SME noted the positive intention behind this but that it would be necessary to consider if the means to obtain this does not already exist.

Annual Reporting

- Annual System Incidents Report

OC3.6.4 Using best endeavours, The Company shall produce an annual report at latest 1 month after the end of the 12-month reporting period, this Annual System Incidents Report shall:

a) review and examine all the data in the previous 12 months of System Incidents Reports;

b) compare trends to previous 12-month periods;

c) highlight the most Significant Events and learnings from these;

d) look for any trends or emerging issues for the System;

e) publish analysis of frequency duration data and trends;

f) provide updates on new or improved measurements and data collection and analysis on the System;

g) request feedback from industry on analysis, learnings and trends.

The Company shall and present the Annual System Incidents Report to the Grid Code Review Panel and publish the report on the Website inviting comments for improvements and omissions which shall be considered and addressed in the following Annual System Incidents Report.

The Proposer has introduced a new section for annual reports to analyse trends and significant events. The NESO SME expressed concern around duplication with the existing reports, annual report on load-frequency control (LFC) and the annual report on the incident classification scale (ICS).  One Workgroup member recommended NESO use generic naming 'incident report' terminology instead of the Modification reference that led to their creation, referencing the current NESO use of GC0105 and GC0151 System Incidents Reports.

NESO Data Sharing and Ofgem’s Data Best Practice Guidance

The NESO SME outlined the organisation's comprehensive four-tier data classification framework, which categorises information as public, general, confidential, or strictly confidential. This system governs the labelling and management of data based on its sensitivity, providing clear protocols for storage, access control, and physical security. The framework is designed to ensure strict adherence to Ofgem's data best practice requirements as well as NESO's internal ringfencing policies.

NESO SME also outlined the data sharing triage process, which systematically evaluates each request by assessing applicable legal constraints and a range of risks, including security, commercial, privacy, and reputational factors. Additionally, the process requires obtaining consent from relevant third parties, such as TOs. Each assessment is thoroughly documented and subjected to review by both risk specialists and legal counsel, ensuring that openness is maximised while all identified risks are effectively mitigated.

During the discussion, a Workgroup member questioned the scope of data sharing. The NESO SME explained that NESO escalates high risk situations to market monitoring to prevent any violations, particularly in the absence of a Non Disclosure Agreement (NDA). Another member stressed the necessity of making data widely available to prevent potential market manipulation. In response, the SME reaffirmed NESO’s commitment to transparency and its rigorous approach to reviewing triage decisions.

During the discussion, a Workgroup member expressed reservations regarding the distribution of raw PMU data, citing concerns about reputational and legal implications should specific incidents be linked to identifiable assets. In response, the SME clarified that NESO’s triage process is designed to identify and address such risks, ensuring that any data sharing is contingent upon obtaining consent from TOs and implementing appropriate risk mitigation measures. Furthermore, data classified as strictly confidential is subject to enhanced controls to safeguard its integrity and security.

It was emphasised that NESO conducts annual reviews of recurring data sharing arrangements to reassess the associated risk profiles, with provisions for more frequent evaluations should risk factors evolve or new concerns arise. Following the triage and approval process, data is disseminated in accordance with its designated classification. NESO is also committed to promoting transparency by proactively publishing data deemed low risk on its public portal.

The Workgroup debated whether to publish raw datasets or summary reports, with the NESO SME favouring summary reports for clarity. Thresholds were also discussed (e.g., 250 MW loss, 0.1 Hz/s RoCoF), alongside potential automation criteria and avoiding redundant reporting; NESO also suggested potential changes to region definitions and data intervals.

NESO Data triage process

The Workgroup discussed the complexities of data ownership, the triage process for sharing PMU data, and the challenges in publishing high resolution data. The Workgroup questioned current practices and advocating for greater openness and alignment with best practice obligations. NESO explained that while data is presumed open, NESO must conduct a triage process to determine if PMU data can be shared, considering confidentiality and potential system vulnerabilities, and requiring permission from TOs.

The Proposer and a Workgroup member highlighted that since PMU data is funded by consumers and falls under best practice obligations, TOs should be publishing it, and the Workgroup should focus on ensuring compliance with these obligations rather than restricting publication due to security concerns. NESO clarified that it receives limited PMU data, much of which is not yet operational or of sufficient quality for publication, and that the TOs are responsible for the original data, with NESO producing reports based on their analysis.

The Workgroup discussed the status and future rollout of PMU installations, the feasibility of meeting the reporting requirements being proposed, and the importance of regional data coverage. NESO clarified that while some PMU data is being received, it is still in the testing phase and not operational, with full rollout expected to begin after Q1 2026. One Workgroup member emphasised the need for regional diversity in PMU data to ensure meaningful analysis, suggesting alignment with existing regional boundaries used in system operability frameworks, and the Proposer supported flexibility in the number of regions as more PMUs come online. One Workgroup member noted that the expected timeline for PMU rollout aligns with the requested implementation of GC0181 and queried when sufficient PMUs would be operational to meet the reporting requirements.

Sharing PMU data and installations

The NESO SME provided an update on whether TO data can be published and where it could best be accessed.  Noting practicality and constraints around sharing PMU data more widely and in real time. Key issues raised were:

- clarification needed on what confidentiality constraints restrict data access, noting that the term is often used vaguely. TOs should not assume generators’ views and that any objections must come directly from the source;

- both TOs and Generators have concerns about commercial sensitivity, particularly where data may reveal generator-specific issues. Noting that full User buy-in would be required before sharing certain data;

- suggestions of any confidentiality objections must be provided in writing by the party asserting them, rather than relying on verbal reports or assumptions;

- the validity of confidentiality concerns, noting that PMU data at substations is consumer-funded and should not easily identify individual generators. Practical justification of how confidentiality applies and who is raising the concern was needed.

A Workgroup member queried as to why TOs would incur any costs, since PMUs are already installed and data is already shared with NESO, suggesting TOs may not need to do anything beyond current practices.  They also stated that the rollout and sharing of data should be managed by NESO, as the data is already available in-house. Any solution or costing should be NESO's responsibility rather than the TOs'.

The NESO SME advised the Workgroup that NGET are considering timelines for the full PMU rollout, noting that Scotland's rollout is complete, and other regions are expected to follow, with significant progress anticipated by March 2026 and completion targeted by the end of 2027.

The NESO SME also mentioned that the same timeline applies to frequency, inertia and system resolution data and by December 2027, there should be sufficient rollout to access the necessary data.

A map was presented showing current and planned PMU installations, including their locations, numbers, zones and types would be useful to provide clarity on current and future PMUs; and Further information regarding PMUs being installed that are of the same technology or specification and to clarify their technical capabilities was requested.

NESO’s SME noted that two TOs are generally open to sharing data but have raised concerns regarding commercial sensitivity and liability. One TO has not yet provided a specific response on confidentiality. Despite these concerns, all TOs currently supply data to NESO according to existing agreements.

TOs were not able to provide definitive cost estimates for the proposed system changes. One sought input from their internal teams, while another indicated they would prefer to wait until further PMU deployment before estimating costs. Overall, there is a general understanding that the resource requirements may be substantial, but specific details are still uncertain.

The Workgroup reviewed the requirements outlined in STCP 27-1, which obligate TOs to provide incident-related information to NESO. Members discussed whether these procedures should be further formalised or automated, aiming to enhance efficiency and ensure the process remains robust and adaptable for future needs. Any data requirements proposed though GC0181 will need to be aligned with STCP 27-1 and it will be determined if a modification to the STC is needed to codify information exchange from TOs to NESO and onwards from NESO.

At a later Workgroup, the Proposer raised concerns about inconsistent and contradictory information regarding PMU rollout and data availability, noting difficulty progressing work due to unclear inputs. A Workgroup member suggested submitting a Freedom of Information request to clarify industry compliance with PMU installation deadlines set out in the STC, noting uncertainty about whether NESO or TOs are responsible and the lack of clarity on industry-wide adherence.

PMU Technical Specifications and Standards Alignment

The NESO SME clarified that PMUs installed across the network come from different manufacturers, but all are required to meet established minimum standards, specifically IEEE C37.118-2005. This standard ensures PMUs report at a rate of 10 frames per second for 50 Hz systems and defines acceptable limits for measurement errors in frequency, phase angle, and harmonic distortion.

A Workgroup member highlighted that Appendix B of STCP 27-1 specifies the need for higher update rates specifically, 25 Hz and the collection of post-event waveform data. The Workgroup member questioned whether TOs are deploying Class P or Class M PMUs and recommended that the Workgroup request more detailed information regarding the actual equipment installed to ensure compliance with these requirements.

The Workgroup recognised that the referenced IEEE standard from 2005 is now outdated, as a newer 2018 version is available. It was agreed that recommending an update would help ensure alignment with current best practices and regulatory requirements.

At Workgroup 7, NESO confirmed that a review of IEEE PMU standards had been undertaken, identifying that PMUs across GB operate to a mix of 2005, 2011, 2014 and 2018 versions, with the 2014/2018 standards broadly aligned. NESO have committed to providing a written summary of this, and to clarify implications for compliance and any required updates to related documents.

PMU Deployment, Regional Coverage, and Data Confidentiality

NESO Representative outlined the current approach to mapping PMU installations across Grid Supply Point (GSP) zones. Each zone is equipped with two PMUs to ensure redundancy and reliability. Frequency measurements from these PMUs will be consolidated into five regional values for system monitoring. However, the specific alignment of these regions with restoration areas has not yet been finalized and will require further clarification.

A Workgroup member identified possible gaps in PMU coverage, especially near HVDC links and offshore wind farm connection points. The member requested that TOs confirm their future installation plans to help ensure the system is comprehensively monitored.

NESO presented an initial view of current and planned HVDC links and PMU locations via mapping material, noting limitations in visualising all locations. NESO agreed to provide an updated approach using an itemised list of PMU locations alongside revised mapping.

NESO SME explained that, although certain site-specific details must remain confidential, the primary concern centres on sharing sensitive data such as manufacturer and model information rather than general GSP locations. The SME assured the Workgroup that all non-confidential information will be made available whenever possible.

GB alignment with Worldwide Reporting Practices and European Standard

NESO presented findings on worldwide reporting practices and shared that in Europe, Australia, New Zealand, Japan, and North America typically require incident reporting within 30 calendar days or 20 business days and found no examples of any country currently reporting within one week as proposed. The Workgroup raised questions about the alignment of UK sampling rates with European requirements, specifically the move from one second to 0.5 seconds, and the need for dynamic alignment under the UK-EU agreement, NESO agreed to investigate further. One Workgroup member proposed that instead of focusing solely on post-incident reporting, the Workgroup consider continuous publication of regional frequency data at high resolution, which could simplify processes and provide greater value to stakeholders.

The NESO SME explained that GB currently aligns with European requirements for frequency data resolution, which is set at one second for frequency quality analysis, referencing Article 131.1A. The one-second resolution is used for frequency quality checks and event analysis, while frequency control in Europe uses lower resolutions (one minute and fifteen minutes). There is no RoCoF reporting requirement in the referenced European standards.

A Workgroup member queried whether network operators in Europe might be operating at higher standards than the legislative minimum, suggesting the need to check with actual operators for current practices and direction of travel. Following this, NESO shared findings from discussions with European TSOs, noting disparities in data reporting and sampling rates.

The NESO SME acknowledged that only the legislation was checked and not actual operator practices.  It was also clarified that the one millihertz requirement in Article 130 relates to measurement accuracy, not time resolution.

The Workgroup discussed that GB could potentially achieve better than one-second resolution if tools allow, which would exceed current European requirements.

NESO’s Representative noted that EirGrid and Energinet release frequency data at different intervals, usually with a delay of one to two months. Additionally, ENTSO-E requires data submissions from TOs on a quarterly basis, along with annual public reports. Most TOs do not currently report as frequently as proposed in GB.

NESO Representative committed to regularly informing the Workgroup about any updates or advancements in international practices.

Monitoring Capabilities

Implementation Considerations

- PMU progress

- Website

- NESO flagged considerations on tools, analysis and operational work required

Based on feedback within the Workgroup, the Proposer has refined legal text drafting to allow for reporting to be provided as and when data developments are made available, rather than working to a fixed delivery deadline. A Workgroup Observer noted that within the proposed solution, all data requested is available from current or planned instrumentation.

Electrical Standards

The Workgroup has considered the interaction with the Electrical Standard and consider that any wider work required would be separate from the Modification. Further detail needed

Draft legal text

Workgroup Consultation question X: Xxxxx?

## Alternative Requests

A number of Alternative Requests were submitted by Workgroup members (Annex XX).

These Requests set out the case as to why the party or Workgroup member who submitted them wished to amend parts of the Original Proposal.

The Workgroup reviewed all of these Requests, and the table below provides an overview of each Request (and who raised it) along with its status.

Throughout the Workgroup discussion, XX Alternative Requests were raised, XX of these were voted to become Workgroup Alternatives (WACMs/ WAGCMs/ASMs), with Alternative Request X becoming WACMX/ WAGCMX/ASMX and Alternative Request X becoming WACMX/ WAGCMX/ASMX. It was later agreed by the Workgroup (at Workgroup meeting XX on DD Month Year) not to continue developing WACMX/ WAGCMX/ASMX as an option, and so it was withdrawn.

| Solution and Outcome of Alternative Vote | Party | Characteristic | Mechanism of Workgroup Vote |
| --- | --- | --- | --- |
| Alternative Request 1 (WACMX/ WAGCMX/ASMX) |  |  | Voted in by Workgroup/ Not saved by the Workgroup Chair/ Saved by the Workgroup Chair as may better facilitate the AO |
| Alternative Request 2 (WACMX/ WAGCMX/ASMX) |  |  | Voted in by Workgroup/ Not saved by the Workgroup Chair/ Saved by the Workgroup Chair as may better facilitate the AO |
| Alternative Request 3 (WACMX/ WAGCMX/ASMX) |  |  | Voted in by Workgroup/ Not saved by the Workgroup Chair/ Saved by the Workgroup Chair as may better facilitate the AO |

[Workgroup Alternative Number] – [Title]

Overview: [Take from the Alternative Request Form unless there have been any changes, this should not be the full solution as that will be detailed in the solution section]

Workgroup discussion: [Include Workgroup discussion, you can also bookmark to another relevant section]

Consideration of other options

The NESO representative suggested an alternative to the Proposers’ proposed legal text, aiming to reconcile the Workgroup's objectives with what is technically and operationally feasible, and invited feedback from the Workgroup and the Proposer on key points such as the number of regions, reporting frequency, and data resolution.

The Workgroup discussion focused on achievable solutions, futureproofing, and the balance between ambition and practicality. Several Workgroup members suggested wording to allow for the addition of more regions as PMU data becomes available and to align data resolution requirements with existing obligations, ensuring the modification remains relevant as technology and practices evolve. NESO clarified that sharing individual PMU measurements poses challenges, but publishing aggregated or representative frequency data at the required resolution is feasible, and that the main obstacles are process changes and alignment with international standards.

To include NESO summary table highlighting key differences

Workgroup consultation question X: Xxxxx?

## Workgroup Alternative 1 solution

This is the Proposer’s area. If this has been updated in the Proposal form take what has been drafted and speak with the Proposer to update into plain English to add clarity if it’s not as clear as it could be. This should be an overview of what the current thinking/solution is.

Workgroup Consultation question X: Xxxxx?

## Workgroup Alternative 2 solution

This is the Proposer’s area. If this has been updated in the Proposal form take what has been drafted and speak with the Proposer to update into plain English to add clarity if it’s not as clear as it could be. This should be an overview of what the current thinking/solution is .

Workgroup Consultation question X: Xxxxx?

Draft legal text

Legal text will be drafted after the Workgroup Consultation has been completed.

or

The draft legal text for this change can be found in Annex xx.

Figure X below illustrates the difference between each of the solutions (for further detail see Annex XX)

|  | Legal text title | Legal text title | Legal text title | Legal text title |
| --- | --- | --- | --- | --- |
| Original |  |  |  |  |
| WACMX/ WAGCMX/ASMX |  |  |  |  |
| WACMX/ WAGCMX/ASMX |  |  |  |  |
| WACMX/ WAGCMX/ASMX |  |  |  |  |

The following considerations were taken into account when creating the draft legal text:

- [Discussion topic]: [Outcome]

- [Discussion topic]: [Outcome]

- [Discussion topic]: [Outcome]

Workgroup Consultation question X: Xxxxx?

What is the impact of this change?

| ## Proposer’s assessment against Grid Code Objectives |  |
| --- | --- |
| Relevant Objective | Identified impact |
| (i) To permit the development, maintenance and operation of an efficient, coordinated and economical system for the transmission of electricity; | Positive This change means that the energy system can operate more safely and reliably now and in the future in a way that benefits end Consumers. |
| (ii) Facilitating effective competition in the generation and supply of electricity (and without limiting the foregoing, to facilitate the national electricity transmission system being made available to persons authorised to supply or generate electricity on terms which neither prevent nor restrict competition in the supply or generation of electricity); | Neutral |
| (iii) Subject to sub-paragraphs (i) and (ii), to promote the security and efficiency of the electricity generation, transmission and distribution systems in the national electricity transmission system operator area taken as a whole; | Positive This change means that the energy system can operate more safely and reliably now and in the future in a way that benefits end Consumers. |
| (iv) To efficiently discharge the obligations imposed upon the licensee by this license* and to comply with the Electricity Regulation and any relevant legally binding decisions of the European Commission and/or the Agency; and | Neutral |
| (v) To promote efficiency in the implementation and administration of the Grid Code arrangements | Neutral |
| * See Electricity System Operator Licence |  |

## Original and Workgroup Alternative Proposer’s assessment against Code Objectives

From the Proposal form and any Workgroup Alternates request forms – update with any amends

| Original Proposer’s assessment against XXX Code Objectives |  |
| --- | --- |
| Relevant Applicable Objective | Identified impact |

| Relevant Applicable Objective | WACMX/ WAGCMX/ASMX Proposer’s assessment | WACMX/ WAGCMX/ASMX Proposer’s assessment | WACMX/ WAGCMX/ASMX Proposer’s assessment | WACMX/ WAGCMX/ASMX Proposer’s assessment |
| --- | --- | --- | --- | --- |
| - i) |  |  |  |  |

| ## Proposer’s assessment of the impact of the modification on the stakeholder / consumer benefit categories |  |
| --- | --- |
| Stakeholder / consumer benefit categories | Identified impact |
| Improved safety and reliability of the system | Positive ​​This change mean that the energy system can operate more safely and reliably now and in the future in a way that benefits end Consumers |
| Lower bills than would otherwise be the case | Neutral |
| Benefits for society as a whole | Positive The recent Spanish Blackout around 12:35 on April 28, 2025 demonstrates the reliance of the society on a safe and secure electricity grid. |
| Reduced environmental damage | ​​Neutral |
| Improved quality of service | Neutral |

When will this change take place?

Implementation date

10 Business days after Authority decision

Proposer’s justification of Implementation date

The modification should be able to be developed quickly before consultation, as draft legal text has been provided. It should not take long to implement.

Date decision required by

As soon as possible.

Implementation approach

The existing processes to operate OC3.4 to be updated.

Proposer’s justification for governance route

Governance route: Standard Governance modification with assessment by a Workgroup.

The Proposer originally recommended a Self-Governance Modification as the Proposer did not think that the proposed solution would have a material impact on industry parties. At the Grid Code Review Panel (GCRP) on 21 August 2025, it was decided the Governance route be changed to Standard Governance with assessment by a Workgroup.

Interactions

# Interactions

| ​​☐CUSC | ​​☐​BSC | ​​☐STC | ​​☐​SQSS |
| --- | --- | --- | --- |
| ​​☐​European Network Codes | ​​☐ EBR Article 18 T&Cs1 | ​​☐​Other modifications | ​​☐​Other |

No interactions.

How to respond

Standard Workgroup Consultation questions

- Do you believe that the Original Proposal and/or any potential alternatives better facilitate the Applicable Objectives versus the current baseline?

- Do you support the proposed implementation approach?

- Do you have any other comments?

- Do you wish to raise a Workgroup Consultation Alternative request for the Workgroup to consider?

- Does the draft legal text satisfy the intent of the modification?

- Do you agree with the Workgroup’s assessment that the modification does/does not impact the European Electricity Balancing Regulation (EBR) Article 18 terms and conditions held within the Code?

- Do you have any comments on the impact of the modification on the EBR Objectives?

Specific Workgroup Consultation questions

- How do you currently use data reported under OC3?

- Would actions change with faster, more frequent, more granular and wider-area reporting proposed?

- What industry and/or consumer benefits do you anticipate?

- Do you agree that the proposed legal text preserves flexibility for future publication formatting changes?

The Workgroup is seeking the views of Grid Code Users and other interested parties in relation to the issues noted in this document and specifically in response to the questions above.

Please send your response to grid.code@neso.energy using the response pro-forma which can be found on the GC0181 modification page.

In accordance with Governance Rules if you wish to raise a Workgroup Consultation Alternative Request please fill in the form which you can find at the above link.

If you wish to submit a confidential response, mark the relevant box on your consultation proforma. Confidential responses will be disclosed to the Authority in full but, unless agreed otherwise, will not be shared with the Panel, Workgroup or the industry and may therefore not influence the debate to the same extent as a non-confidential response.

Acronyms, key terms and reference material

| Acronym / key term | Meaning |
| --- | --- |
| BSC | Balancing and Settlement Code |
| CDCL | Cottam Development Centre Limited |
| CUSC | Connection and Use of System Code |
| EBR | Electricity Balancing Regulation |
| FOI | Freedom of Information |
| GC | Grid Code |
| GCDF | Grid Code Development Forum |
| GCRP | Grid Code Review Panel |
| HVDC | High Voltage Direct Current |
| OC | Operating Code |
| PC | Planning Code |
| RoCoF | Rate of Change of Frequency |
| STC | System Operator Transmission Owner Code |
| SQSS | Security and Quality of Supply Standards |
| T&Cs | Terms and Conditions |

Reference material

- GCDF presentation slides

- Project REV WP2 report

- ENTSOE Iberian blackout report.

- IFA2 interconnector trip

Annexes

| Annex | Information |
| --- | --- |
| Annex 01 | GC0181 Proposal form |
| Annex 02 | GC0181 Terms of reference |
| Annex 03 | GC0181 Draft Legal Text |
| Annex 04 | Freedom of Information request response FOI/25/321 |
| Annex 05 | Freedom of Information request response FOI/26/021 |
| Annex 06 | Phase Jump Incident Reporting Sygensys Input to GC0181 |
| Annex 0X | Update as required |

https://assets.publishing.service.gov.uk/government/uploads/system/uploads/attachment_data/file/855767/e3c-gb-power-disruption-9-august-2019-final-report.pdf

https://www.neso.energy/industry-information/codes/gc/modifications/gc0105-system-incidents-reporting

https://www.neso.energy/industry-information/codes/gc/modifications/gc0151-grid-code-compliance-fault-ride-through-requirements

https://www.neso.energy/industry-information/codes/security-and-quality-supply-standard-sqss/frequency-risk-and-control-report-frcr

https://www.neso.energy/industry-information/codes/gc/modifications/gc0105-system-incidents-reporting

https://www.solarpowerportal.co.uk/energy-storage/ifa-interconnector-fault-causes-49-2hz-frequency-event

https://www.neso.energy/document/300661/download

https://www.neso.energy/industry-information/industry-data-and-reports/system-performance-reports

https://www.neso.energy/document/354911/download

https://www.entsoe.eu/publications/blackout/28-april-2025-iberian-blackout/

https://www.neso.energy/data-portal/system-inertia