## Winter
The following section details the studies that have been carried out for winter peak. The analysis has been carried out by three TO's on different boundaries, for different generation backgrounds and in different years relative to major transmission assets. For example the pre- series and shunt compensation studies are carried out against 2014/15 demand backgrounds and post Western Link is against a 2016/17 demand background. The focus of the study is on boundary transfers and the ability to meet demand in different system areas. For each one of these studies many transmission contingenicies are performed. These contingincies are network faults on different circuits of the transmission system relative to that boundary. Normally for a boundary there will be between 10-40 contingincies depending on the size (no. of circuit crossing the boundary). Meaning that for each one of the backgrounds listed below there are 10-40 power system studies completed. B6 and B5 boundary studies N-D studies are performed and N-1-1 (where cables are in a particular circuit for example the Western Link). Boundaries B0, B1, B2 & B3 tested against N-1 for winter Boundary B4 tested against N-1 & N-D for winter
Boundary B6
Pre-Series and shunt compensation
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR
Boundary B5
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR
Boundary B4 - B0 are not sensitive to the Series and shunt compensation
Boundary B6
Post - Series and shunt compensation
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR
Boundary B5
Post-Series and Shunt compensation
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR
Boundary B4 - B0 are not sensitive to the Series and shunt compensation
Boundary B4
without Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B3
without Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B2
without Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B1
without Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B0
without Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B4
with Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B3
with Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B2
with Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B1
with Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B0
with Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B6
With Western Link
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR
Boundary B5
With Western Link
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR

## Summer Peak
The following section details the studies that have been carried out for summer peak. The analysis has been carried out by three TO's on different boundaries, for different generation backgrounds and in different years relative to major transmission assets. The focus of the study is on boundary transfers and the ability to meet demand in different system areas. For each one of these studies many transmission contingenicies are performed. These contingincies are network faults on different circuits of the transmission system relative to that boundary. Normally for a boundary there will be between 10-40 contingincies depending on the size (no. of circuit crossing the boundary). B6 and B5 boundary studies N-D studies are performed and N-1-1 for all circuits now Boundaries B0, B1, B2 & B3 tested against N-1 & N-1-1 for summer Boundary B4 tested against N-1 & N-D & N-1-1 & N-1-D for summer
Boundary B6
Pre-Series and shunt compensation
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR
Boundary B5
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR
Boundary B4 - B0 are not sensitive to the Series and shunt compensation
Boundary B6
Post - Series and shunt compensation
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR
Boundary B5
Post-Series and Shunt compensation
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR
Boundary B4 - B0 are not sensitive to the Series and shunt compensation
Boundary B4
without Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B3
without Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B2
without Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B1
without Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B0
without Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B4
with Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B3
with Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B2
with Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B1
with Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B0
with Beaully-Denny and Western Link
Agreed generation dispatch
No foyers sensitivity
No generation in SHE Transmission area at all
Boundary B6
With Western Link
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR
Boundary B5
With Western Link
Hunterston on | Torness off | Heysham on | Hartlepool off | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartelpool on | All other backgrounds as per ToR
Hunterston on | Torness off | Heysham off | Hartlepool on | All other backgrounds as per ToR
Hunterston off | Torness on | Heysham on | Hartlepool on | All other backgrounds as per ToR

## Summer minimum
The following section details the studies that have been carried out for summer minimum. The analysis has been carried out by three TO's in different areas of the system, for different generation backgrounds and levels of embedded generation. The key purpose of the analysis was to determine the networks ability to control the voltage within industry set limits. For each one of these studies many transmission contingenicies are performed. These contingincies are network faults on different circuits (and reactive compensation elements) of the transmission system relative to that boundary. In the areas there were the following contingincies performed for each study background: SHE-Transmission - 260 SP-Transmission - 415 NGET-140
NGET Transmission area
Intact system conditions without new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
2 x Hunterston | No Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
2 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc | No Hartlepool
Intact system conditions new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
Outage system conditions without new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
Outage system conditions new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
SP Transmission area
Intact system conditions without new reactors
2 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
2 x Hunterston | 1 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
2 x Hunterston | 1 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc | No wind
1 x Hunterston | 1 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead (@400MW only) | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead (@400MW only) | All other gen as per methodology and assumptions doc | 10% embedded wind
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead (@400MW only) | All other gen as per methodology and assumptions doc | 40% embedded wind
Intact system conditions new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
2 x Hunterston | 1 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 1 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
2 x Hunterston | 1 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc | No wind
Outage system conditions without new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
Outage system conditions new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
SHE Transmission area
Intact system conditions without new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead (@400MW only) | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead (@400MW only) | All other gen as per methodology and assumptions doc | 10% embedded wind
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead (@400MW only) | All other gen as per methodology and assumptions doc | 40% embedded wind
Intact system conditions new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
Outage system conditions without new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | No Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | No Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
1 x Hunterston | 2 x Torness | 1 x Longannet | 1 x Peterhead | All other gen as per methodology and assumptions doc
Outage system conditions new reactors
1 x Hunterston | 2 x Torness | No Longannet | No Peterhead | All other gen as per methodology and assumptions doc