## Example Dynamic Data Format
Provider | Company Name
Date | xx-xx-xxxx |  |  | Dynamic test data should be submitted to National Grid in this format.
Test | 1
Service | Low Frequency Dynamic Response
Location | AA
Site/Group/Plant | A
Time | Injected Frequency (Hz) | Baseline Power (MW/kW) | Measured Power (MW)
0 | 50 | 0 | 0
0.1 | 50 | 0 | 0
0.2 | 50 | 0 | 0
0.3 | 50 | 0 | 0
0.4 | 50 | 0 | 0
0.5 | 50 | 0 | 0
0.6 | 50 | 0 | 0
0.7 | 50 | 0 | 0
0.8 | 50 | 0 | 0
0.9 | 50 | 0 | 0
1 | 50 | 0 | 0
1.1 | 50 | 0 | 0
1.2 | 50 | 0 | 0
1.3 | 50 | 0 | 0
1.4 | 50 | 0 | 0
1.5 | 50 | 0 | 0
1.6 | 50 | 0 | 0

## Test 1
Test 1
Time (s) | Injected Frequency (Hz) | Increase | Deadband | Deadband
0 | 50 | 0 | 50.015 | 49.985
30 | 50 | 500 | 50.015 | 49.985
30 | 50.02 | 1000 | 50.015 | 49.985
210 | 50.02 | 1500 | 50.015 | 49.985
210 | 50 | 2000 | 50.015 | 49.985
240 | 50 | 2500 | 50.015 | 49.985
240 | 49.98 | 3000 | 50.015 | 49.985
420 | 49.98 | 3500 | 50.015 | 49.985
420 | 50 | 4000 | 50.015 | 49.985
450 | 50
450 | 50.1
630 | 50.1
630 | 50
660 | 50
660 | 49.9
840 | 49.9
840 | 50
870 | 50
870 | 50.2
1050 | 50.2
1050 | 50
1080 | 50
1080 | 49.8
1260 | 49.8
1260 | 50
1290 | 50
1290 | 50.3
1470 | 50.3
1470 | 50
1500 | 50
1500 | 49.7
1680 | 49.7
1680 | 50
1710 | 50
1710 | 50.4
1890 | 50.4
1890 | 50
1920 | 50
1920 | 49.6
2100 | 49.6
2100 | 50
2130 | 50
2130 | 50.5
2310 | 50.5
2310 | 50
2340 | 50
2340 | 49.5
2520 | 49.5
2520 | 50
2550 | 50
1.1
1.2
1.3
1.4
1.5
1.6
1.7
1.8
1.9
1.10
1.11
1.12

## Test 2.1
Test 2.1
Time (s) | Injected Frequency (Hz)
0 | 50
30 | 50
30 | 50.6
80 | 50.6
85 | 50.4
90 | 50.2
95 | 50
100 | 49.8
105 | 49.6
110 | 49.4
160 | 49.4
160 | 50
190 | 50

## Test 2.2
Test 2.2
Time (s) | Injected Frequency (Hz)
0 | 50
30 | 50
30 | 49.4
80 | 49.4
85 | 49.6
90 | 49.8
95 | 50
100 | 50.2
105 | 50.4
110 | 50.6
160 | 50.6
160 | 50
190 | 50

## Test 2.3
Test 2.3
Time (s) | Injected Frequency (Hz)
0 | 50
30 | 50
30 | 50.6
80 | 50.6
95 | 50.4
110 | 50.2
125 | 50
140 | 49.8
155 | 49.6
170 | 49.4
220 | 49.4
220 | 50
250 | 50

## Test 2.4
Test 2.4
Time (s) | Injected Frequency (Hz)
0 | 50
30 | 50
30 | 49.4
80 | 49.4
95 | 49.6
110 | 49.8
125 | 50
140 | 50.2
155 | 50.4
170 | 50.6
220 | 50.6
220 | 50
250 | 50

## Test 3.1
Test 3.1
Time (s) | Injected Frequency (Hz)
0 | 50
30 | 50
30 | 50.6
1830 | 50.6
1830 | 50
1860 | 50

## Test 3.2
Test 3.2
Time (s) | Injected Frequency (Hz)
0 | 50
30 | 50
30 | 49.4
1830 | 49.4
1830 | 50
1860 | 50

## Test 4
Test 4 | Note: For this test the system frequency should be used as the frequency injection, thus there is no table to display. This example given lasts for 900 seconds but the test should be carried out for 3600 seconds.

## Example Static Data Format
Provider | Company Name
Date | xx-xx-xxxx |  |  |  | Single static test data should be submitted to Nataional Grid in this format
Test | 1
Service | Low Frequency Non-Dynamic Secondary Response
Location | AA
Site/Group/Plant | A
Time | Injected Frequency (Hz) | Baseline Power (MW) | Measured Power (MW) | Relay
0 | 50 | 0 | 0 | 0
0.1 | 50 | 0 | 0 | 0
0.2 | 50 | 0 | 0 | 0
0.3 | 50 | 0 | 0 | 0
0.4 | 50 | 0 | 0 | 0
0.5 | 50 | 0 | 0 | 0
0.6 | 50 | 0 | 0 | 0
0.7 | 50 | 0 | 0 | 0
0.8 | 50 | 0 | 0 | 0
0.9 | 50 | 0 | 0 | 0
1 | 50 | 0 | 0 | 0
1.1 | 50 | 0 | 0 | 0
1.2 | 50 | 0 | 0 | 0
1.3 | 50 | 0 | 0 | 0
1.4 | 50 | 0 | 0 | 0
1.5 | 50 | 0 | 0 | 0
1.6 | 50 | 0 | 0 | 0

## Example Static Data Format 2+
Provider | Company Name
Date | xx-xx-xxxx | [8 empty] | Multiple static test data should be submitted to National Grid in this format
Test | 1
Service | Low Frequency Non-Dynamic Secondary Response
Location | AA |  |  |  | AB
Site/Group/Plant | A |  |  |  | B
Time | Injected Frequency (Hz) | Baseline Power (MW) | Measured Power (MW) | Relay | Time | Injected Frequency (Hz) | Baseline Power (MW) | Measured Power (MW) | Relay
0 | 50 | 0 | 0 | 0 | 0 | 50 | 0 | 0 | 0
0.1 | 50 | 0 | 0 | 0 | 0.1 | 50 | 0 | 0 | 0
0.2 | 50 | 0 | 0 | 0 | 0.2 | 50 | 0 | 0 | 0
0.3 | 50 | 0 | 0 | 0 | 0.3 | 50 | 0 | 0 | 0
0.4 | 50 | 0 | 0 | 0 | 0.4 | 50 | 0 | 0 | 0
0.5 | 50 | 0 | 0 | 0 | 0.5 | 50 | 0 | 0 | 0
0.6 | 50 | 0 | 0 | 0 | 0.6 | 50 | 0 | 0 | 0
0.7 | 50 | 0 | 0 | 0 | 0.7 | 50 | 0 | 0 | 0
0.8 | 50 | 0 | 0 | 0 | 0.8 | 50 | 0 | 0 | 0
0.9 | 50 | 0 | 0 | 0 | 0.9 | 50 | 0 | 0 | 0
1 | 50 | 0 | 0 | 0 | 1 | 50 | 0 | 0 | 0
1.1 | 50 | 0 | 0 | 0 | 1.1 | 50 | 0 | 0 | 0
1.2 | 50 | 0 | 0 | 0 | 1.2 | 50 | 0 | 0 | 0
1.3 | 50 | 0 | 0 | 0 | 1.3 | 50 | 0 | 0 | 0
1.4 | 50 | 0 | 0 | 0 | 1.4 | 50 | 0 | 0 | 0
1.5 | 50 | 0 | 0 | 0 | 1.5 | 50 | 0 | 0 | 0
1.6 | 50 | 0 | 0 | 0 | 1.6 | 50 | 0 | 0 | 0

## Non-Dynamic Low Frequency
Non-Dynamic Low Frequency Response Test
Time (s) | Injected Frequency (Hz)
0 | 50
30 | 50 | 0 | 49.7
40 | 49.72 | 2100 | 49.7
80 | 49.72
90 | 50
120 | 49.5
420 | 49.5
450 | 49.8
750 | 49.8
780 | 49.6
1080 | 49.6
1110 | 50.2
1410 | 50.2
1440 | 50.4
1740 | 50.4
1770 | 50
2010 | 50
2100 | 50
|  |  | 0 | 49.69 | 49.71
|  |  | 2100 | 49.69 | 49.71

## Non-Dynamic High Frequency
Non-Dynamic High Frequency Response Test
Time (s) | Injected Frequency (Hz)
0 | 50
30 | 50
40 | 50.28 |  |  | 0 | 50.3
80 | 50.28 | 0 | 50.31 | 2100 | 50.3
90 | 50 | 2100 | 50.31
120 | 50.5 |  | 50.29
420 | 50.5 |  | 50.29
450 | 50.2
750 | 50.2
780 | 50.4
1080 | 50.4
1110 | 49.8
1410 | 49.8
1440 | 49.6
1740 | 49.6
1770 | 50
2070 | 50
2100 | 50