## Cost RoCoF and VS
[11 empty] | total | 73634579.2 | 77789666.7
[7 empty] | Sites |  | Work Required
Generation Plant Types and Actions Required |  |  | Description |  |  |  | Proportion of all sites | Number of Sites | Change RoCoF protection setting only | Change RoCoF setting with relay change | Site Visit | Total Cost (>=1MVA, <5MVA)
Estimate of numbers affected Low, typical, high |  |  | H | L | T | H
Cost per Site (£) |  |  | Estimated cost per site | [5 empty] | 200 | 7700 | 200
LoM protection is RoCoF |  |  | % of sites use RoCoF - change required | 33% | 50% | 70% | 70% | 683.9 |  |  | 136780
LoM protection is not RoCoF |  |  | % of sites use VS - probably needs to be changed to RoCoF |  |  |  | 30% | 293.1 |  |  | 58620
Synchronous Generators |  |  |  | 50% | 75% | 85% | 85% | 830.45
Asynchronous Generators | [6 empty] | 15% | 146.55
|  | Synch RoCoF |  |  |  |  | 59.5% | 581.315
|  | Synch VS |  |  |  |  | 25.5% | 249.135
|  | Asynch RoCoF |  |  |  |  | 10.5% | 102.585
|  | Synch VS |  |  |  |  | 4.5% | 43.965
RoCoF Setting Only |  |  | % capable of resetting | 95% | 50% | 10% | 7% | 68.39
RoCcoF Relay Change |  |  | % requiring relay change |  |  |  | 63% | 615.51
VS Changes |  |  | %ge of VS sites that cannot be reconfigured; need relay change or removal | 10% | 50% | 90% | 27% | 263.79
VS Changes |  |  | %ge of VS sites that can be reconfigured | 90% | 50% | 10% | 3% | 29.31
Protection Costs:
| Synch - reset RoCoF |  |  | 56.52% | 29.75% | 5.95% | 5.95% | 58.1315 | 11626.3
| Synch replace RoCoF |  |  | 2.975% | 29.75% | 53.55% | 53.55% | 523.1835 |  | 4028512.95
| Synch reset VS to RoCoF |  |  | 22.95% | 12.75% | 2.55% | 2.55% | 24.9135 | 4982.7
| Synch replace VS with RoCoF |  |  | 2.55% | 12.75% | 22.95% | 22.95% | 224.2215 |  | 1726505.55
| Asynch reset RoCoF |  |  | 9.975% | 5.25% | 1.05% | 1.05% | 10.2585 | 2051.7
| Asynch remove RoCof |  |  | 0.525% | 5.25% | 9.45% | 9.45% | 92.3265 | 18465.3
| Asynch reset VS to RoCoF |  |  | 4.05% | 2.25% | 0.45% | 0.45% | 4.3965 | 879.3
| Asynch remove VS |  |  | 0.45% | 2.25% | 4.05% | 4.05% | 39.5685 | 7913.7
Totals | [7 empty] | 977 | 18660.7 | 5755018.5 | 195400 | 5969079.2
[7 empty] | Sites |  | Work Required
Generation Plant Types and Actions Required |  |  | Description |  |  |  | Proportion of all sites | Number of Sites | Change RoCoF protection setting only | Change RoCoF setting with relay change | Site Visit | Total Cost (<1MVA)
Cost per Site (£) |  |  | Estimated cost per site | L | T | H |  |  | 200 | 7700 | 200
LoM protection is RoCoF |  |  | % of sites use RoCoF - change required | 5% | 12% | 14% | 14% | 5413.24 |  |  | 1082648
LoM protection is not RoCoF |  |  | % of sites use VS - no change required |  |  |  | 86% | 33252.76 |  |  | 6650552
Synchronous Generators |  |  |  | 1% | 2.75% | 20% | 20% | 7733.2
Asynchronous Generators | [6 empty] | 80% | 30932.8
|  | Synch RoCoF |  |  |  |  | 2.8% | 1082.648
|  | Synch VS |  |  |  |  | 17.2% | 6650.552
|  | Asynch RoCoF |  |  |  |  | 11.2% | 4330.592
|  | Synch VS |  |  |  |  | 68.8% | 26602.208
RoCoF Setting Only |  |  | % requiring setting only | 95% | 50% | 10% | 1.4% | 541.324
Relay Change |  |  | % requiring releay change |  |  |  | 12.6% | 4871.916
VS Changes |  |  | %ge of VS sites that cannot be reconfigured; need relay change or removal | 10% | 50% | 90% | 77.4% | 29927.484
VS Changes |  |  | %ge of VS sites that can be reconfigured | 90% | 50% | 10% | 8.6% | 3325.276
Protection Costs:
| Synch - reset RoCoF |  |  | 2.66% | 1.4% | 0.28% | 0.28% | 108.2648 | 21652.96
| Synch replace RoCoF |  |  | 0.14% | 1.4% | 2.52% | 2.52% | 974.3832 |  | 7502750.64
| Synch reset VS to RoCoF |  |  | 15.48% | 8.6% | 1.72% | 1.72% | 665.0552 | 133011.04
| Synch replace VS with RoCoF |  |  | 1.72% | 8.6% | 15.48% | 15.48% | 5985.4968 |  | 46088325.36
| Asynch reset RoCoF |  |  | 10.64% | 5.6% | 1.12% | 1.12% | 433.0592 | 86611.84
| Asynch remove RoCof |  |  | 0.56% | 5.6% | 10.08% | 10.08% | 3897.5328 | 779506.56
| Asynch reset VS to RoCoF |  |  | 61.92% | 34.4% | 6.88% | 6.88% | 2660.2208 | 532044.16
| Asynch remove VS |  |  | 6.88% | 34.4% | 61.92% | 61.92% | 23941.9872 | 4788397.44
Totals | [7 empty] | 38666 | 6341224 | 53591076 | 7733200 | 67665500
73634579.2
39643
[7 empty] | Sites |  | Work Required
Generation Plant Types and Actions Required |  |  | Description |  |  |  | Proportion of all sites | Number of Sites | Change RoCoF protection setting only | Change RoCoF setting with relay change | Site Visit | Total Cost (>5MVA)
Cost per Site (£) |  |  | Estimated cost per site | L | T | H |  |  | 200 | 7700 | 200
LoM protection is RoCoF |  |  | % of sites use RoCoF - change required | 33% | 50% | 70% | 70% | 473.9 |  |  | 94780
LoM protection is not RoCoF |  |  | % of sites use VS - no change required |  |  |  | 30% | 203.1 |  |  | 40620
Synchronous Generators |  |  |  | 50% | 75% | 85% | 85% | 575.45
Asynchronous Generators | [6 empty] | 15% | 101.55
|  | Synch RoCoF |  |  |  |  | 59.5% | 402.815
|  | Synch VS |  |  |  |  | 25.5% | 172.635
|  | Asynch RoCoF |  |  |  |  | 10.5% | 71.085
|  | Synch VS |  |  |  |  | 4.5% | 30.465
RoCoF Setting Only |  |  | % requiring setting only | 95% | 50% | 10% | 7% | 47.39
Relay Change |  |  | % requiring releay change |  |  |  | 63% | 426.51
VS Changes |  |  | %ge of VS sites that cannot be reconfigured | 10% | 50% | 90% | 27% | 182.79
VS Changes |  |  | %ge of VS sites that can be reconfigured | 90% | 50% | 10% | 3% | 20.31
| Synch - reset RoCoF |  |  | 56.52% | 29.75% | 5.95% | 5.95% | 40.2815 | 8056.3
| Synch replace RoCoF |  |  | 2.975% | 29.75% | 53.55% | 53.55% | 362.5335 |  | 2791507.95
| Synch reset VS to RoCoF |  |  | 22.95% | 12.75% | 2.55% | 2.55% | 17.2635 | 3452.7
| Synch replace VS with RoCoF |  |  | 2.55% | 12.75% | 22.95% | 22.95% | 155.3715 |  | 1196360.55
| Asynch reset RoCoF |  |  | 9.975% | 5.25% | 1.05% | 1.05% | 7.1085 | 1421.7
| Asynch remove RoCof |  |  | 0.525% | 5.25% | 9.45% | 9.45% | 63.9765 | 12795.3
| Asynch reset VS to RoCoF |  |  | 4.05% | 2.25% | 0.45% | 0.45% | 3.0465 | 609.3
| Asynch remove VS |  |  | 0.45% | 2.25% | 4.05% | 4.05% | 27.4185 | 5483.7
Totals | [7 empty] | 677 | 31819 | 3987868.5 | 135400 | 4155087.5
Note on F5: Mike Kay: Change this cell L, T, H

## Sheet1
|  | Low |  | Typical |  | High
|  | RoCoF | Other | RoCoF | Other | RoCoF | Other
1MW-5MW | Synch | 97.7 | 654.59 | 361.49 | 488.5 | 635.05 | 293.1
977 | Asynch | 224.71 |  | 127.01 |  | 48.85
|  | Low |  | Typical |  | High
|  | RoCoF | Other | RoCoF | Other | RoCoF | Other
<1MW | Synch | 193.33 | 36732.7 | 483.325 | 34026.08 | 1063.315 | 33252.76
38666 | Asynch | 1739.97 |  | 4156.595 |  | 4349.925