APPENDIX F

TEMPLATE FOR AN EU DCC COMPLIANT DEMAND CONNECTION WITH A STANDARD CONNECTION BOUNDARY (AIS) AT THE BUSBAR CLAMPS.

NOTE THIS TEMPLATE ONLY APPLIES TO TOTALLY NEW DISTRIBUTION SYSTEMS,TRACTION ,NON-EMBEDDED DEMAND AND

DEMAND SIDE BIDDERS WITH AN EU GRID SUPPLY POINT

(NOTES – ALL SECTIONS IN [RED] TO BE SELECTED AS REQUIRED)

ALL SECTIONS IN YELLOW HIGHLIGHTED RED TEXT ARE WHERE A DECISION SHOULD BE MADE DEPENDING ON THE TYPE OF AGREEMENT

ALL SECTIONS IN YELLOW HIGHLIGHTED BLACK ITALLIC TEXT ARE FOR GUIDANCE AND SHOULD BE DELETED BEFORE COMPLETION

NOTE:- WHERE REFERENCE HAS BEEN MADE TO STAGE 1, THIS

ONLY NEEDS TO BE INCLUDED WHERE THE DEVELOPMENT IS STAGED.  IF THERE IS NO REFERENCE TO STAGING THIS REFERENCE CAN BE DELETED

AMENDMENTS RECORD

| Issue | Date | Summary of Changes / Reasons | Authors | Approved by (including Job Title) |
| --- | --- | --- | --- | --- |
| 1 | April 2015 | Update and revision from comments received in 2014 | A Johnson N Martin | G Stein Technical Policy Manager |
| 2 | May 2015 | Updated to include Embedded Generation Issues | A Johnson A Minton | G Stein Technical Policy Manager |
| 3 | January 2016 | Word “record” included in section 8.2 to correct typographical error | A Johnson | G Stein Technical Policy Manager |
| 4 | January 2016 | Additional updates to include Active Network Management and SGT Reverse Power Flow | A Johnson A Minton | G Stein Technical Policy Manager |
| 5 | 17 Nov 2016 | Operational Metering sampling rate change to 1s or 1Hz following customer feedback | A Johnson | Xiaoyao Zhou |
| 6 | 28 Mar 2017 | Addition of “trip relay” column in protection schedule of F4 | Gihan Abeyawardene | Xiaoyao Zhou |
| 7 | 28 Mar 2017 | Update of F3 schedule 1 to reflect Active network management schemes | Dan Clarke | Xiaoyao Zhou |
| 8 | 28 Mar 2017 | Appendix F5 schedule 1, cross-site wiring obligation clarified | A Johnson | Xiaoyao Zhou |
| 9 | 2 Jun 2017 | Update to para 3 of SGT reverse flow section | A Johnson | Xiaoyao Zhou |
| 10 | 24 Oct 2017 | Update to F4 re provision of a protection setting report | G. Abeyawardene | Xiaoyao Zhou |
| 11 | 20 Jul 2018 | Update re TOV and voltage waveform quality | F Ghassemi | Xiaoyao Zhou |
| 12 | 08 Nov 2018 | Addition of EU DCC requirements | A Johnson/F Williams | Xiaoyao Zhou |
| 13 | 27 March 2019 | Updated at the time of the SO/TO split. | F. Williams/E. Ashton | Xiaoyao Zhou |
| 14 | 05 June 2020 | Non-embedded demand guidance clarification | F.Williams | Xiaoyao Zhou |
| 15 | 05 Oct 2020 | Paralleling guidance added to F5 | F Williams | Xiaoyao Zhou |
| 16 | 23 Nov 2020 | EMT requirement added for all non-DNO agreements | D. Clarke/F Williams | Xiaoyao Zhou |
| 17 | 23 Nov 2020 | Requirement to register settlement metering added | D. Clarke/F Williams | Xiaoyao Zhou |
| 18 | 11 June 2021 | Flicker requirement added | F Ghassemi | Xiaoyao Zhou |
| 19 | 16 Dec 2021 | F5 Schedule 2, metering interaction clarification | Oliver Garfield | Xiaoyao Zhou Customer Techical Policy Manager |
| 20 | 13 Dec 2022 | Update to submitted voltage phase unbalance values for traction to align with current practice | A Mosah | Xiaoyao Zhou Customer Techical Policy Manager |
| 21 | 13 Dec 2022 | F5 Schedule 2 recalibration, latency and accuracy requirements added | Stuart Brace | Xiaoyao Zhou Customer Techical Policy Manager |
| 22 | 9 Nov 2023 | Updated to align with NGET TOF | Aisha Yusof | Xiaoyao Zhou Network Operability Policy Manager |
| 23 | 7 Dec 2023 | RMS model requirement added for non-embedded customers | Yuan Chen | Xiaoyao Zhou Network Operability Policy Manager |
| 24 | 27 June 2024 | F5 Power Quality monitoring – references to VT’s in RES documents replaced with description of appropriate CVT type | Iky Rai | Xiaoyao Zhou Customer Techical Policy Manager |
| 25 | 18 Oct 2024 | Electrolyser requirements added | Tony Johnson/Bieshoy Awad | Xiaoyao Zhou Customer Technical Policy Manager |
| 26 | 16 June 2025 | Software quality assurance statement | D. Lacey/J.Fradley | Xiaoyao Zhou Customer Techical Policy Manager |
| 27 | 7 November 2025 | TGN 288 clarification | NGET – Yue Feng | Xiaoyao Zhou Customer Technical Policy Manager |
| 28 | 28 November 2025 | SHE-T metering update | SHE-T | Xiaoyao Zhou Customer Technical Policy Manager |
| 29 | 27 March 2026 | F5 Schedule 2 – metering polarity guidance | Hao Guo | Xiaoyao Zhou Operability Policy Manager |
| 30 | 18 May 2026 | Replacement of fax machine with designated information exchange system following completion of GC0175 | Stuart McLarnon | Xiaoyao Zhou Operability Policy Manager |
| 31 | 18 May 2026 | Removal of ability to site control points out of GB | Anthony Johnson | Xiaoyao Zhou Operability Policy Manager |

(Please delete this page once it has been checked)

APPENDIX F

SITE SPECIFIC TECHNICAL CONDITIONS

CONTENTS

(NOTES – ALL SECTIONS IN [RED] TO BE COMPLETED/DELETED WHERE APPROPRIATE)

| User: | [XXXX] |
| --- | --- |
| Type of User | EU Code User |
| Connection Site: | [XXXX] |

Contents

F1	Agreed Ancillary Services

F2	Derogated Plant

F3	Special Automatic Facilities

F4	Relay Settings & Protection

F5	Other Technical Requirements

Delete the sections in the Electrical Standard paragraph which do not apply.

# Electrical Standards

These appendices contain references to The Scottish Electrical Standards for SPT’s Transmission System (SPTS)/ Scottish Electrical Standards for SHET’s Transmission System (SHETS) or the Relevant Electrical Standards (RES) throughout. The EU Code User shall ensure that all EU Code User equipment contained within the Relevant Transmission Licensee’s busbar protection zone at the User/National Transmission Connection Point (see Grid Code ECC 6.2.1.2) complies with the RES/SPTS/SHETS. The EU Code User shall ensure that subject to the provisions of Grid Code ECC.6.2.1.2 following this agreement, any permanent alterations to all EU Code User equipment contained within the the Relevant Transmission Licensees busbar protection zone at the EU Code User/Relevant Transmission Licensee connection point are agreed between the EU Code User and the Relevant Transmission Licensee. The EU Code User can access the standards from The Company’s website which is available at:-

https://www.neso.energy/industry-information/codes/grid-code-gc/electrical-standards-documents

It is recognised by the EU Code User, the Relevant Transmission Licensee and The Company that the equipment installed at the date of this Agreement may not meet the requirements of the latest SPTS/SHETS or RES but were installed to the standards applicable at the time of design. Accordingly, unless a permanent alteration is made then, the User shall not be required to make the equipment compliant with the SPTS/SHETS or RES and this Appendix F. (this paragraph applies only to existing sites)

The SPTS/SHETS and RES are updated periodically. If the SPTS / SHETS or RES are updated in the period between issuing the Connection Offer and the EU Code User completing the connection to the National Transmission System then The Company will seek agreement with the EU Code User to use the updated RES and SPTS/SHETS as the standard for plant and apparatus at the Connection Point.

APPENDIX F1

SITE SPECIFIC TECHNICAL CONDITIONS

AGREED ANCILLARY SERVICES

| User: | [XXXX] |
| --- | --- |
| Type of User | EU Code User |
| Connection Site: | [XXXX] |

Agreed Ancillary Services

Not applicable - (use this text for DNO or traction agreements but delete if it is DSB/Non-Embedded Customer )

If a Demand Side Bidder /Data Centre/ Non-Embedded Customer include the following text.  If not, delete it.

(DRSC)

There is no requirement for the EU Code User to provide Mandatory Balancing Services. However the EU Code User may wish to declare to The Company their ability to provide Commercial Balancing Services (Agreed Ancillary Services) and the cost of providing such facilities.

There is no obligation to provide these facilities however The Company would recommend that the EU Code User contacts The Company prior to the construction phase of its project to i) discuss the provision of any such services which can be provided and ii) install the necessary hardware (if such additional services are agreed) to allow monitoring facilities to be installed.

Details of the types of Balancing Service and methods of securing them are contained in The Company’s Procurement Guidelines and Balancing Principles. In addition, the User should also be aware that should the User wish to provide a Commercial Balancing Service they will also need to satisfy the applicable requirements of the Grid Code Demand Response Services Code (DRSC).

NOTE there is no requirement for Demand Customers to provide Balancing Services, however should they wish to do so it may be worth including these paragraphs. CHECK WITH CONTRACT SERVICES.

APPENDIX F2

SITE SPECIFIC TECHNICAL CONDITIONS

DEROGATED PLANT

| User: | [XXXX] |
| --- | --- |
| Type of User | EU Code User |
| Connection Site: | [XXXX] |

Derogated Plant

Not applicable.

APPENDIX F3

SITE SPECIFIC TECHNICAL CONDITIONS

SPECIAL AUTOMATIC FACILITIES

| User: | [XXXX] |
| --- | --- |
| Type of User | EU Code User |
| Connection Site: | [XXXX] |

Special Automatic Facilities

- Transmission System to Generating Unit Intertripping Schemes

Not applicable. – unless specified by the TO.  It is not expected that this will apply to traction, non-embedded demand or DSBs.

But, if a BELLA GSP in Scotland, include the following paragraphs

These requirements will largely be dictated by SPT or SHET as defined in the TOCO. When the template has been populated it should be sent to SPT or SHET for checking.

| Category/Substation | Grid Code Ref | CUSC ref | Trip within (ms) | Obligation |
| --- | --- | --- | --- | --- |
|  | BC2.10.2(a) | CUSC4.2A CUSC2.9.3 | (Time determined by TO studies) | See schedule 1 for associated trips/outage combinations |

This Transmission System to Generating Unit(s) intertrip is classified as a category ‘[XXXX]’ intertripping scheme, as defined in the Grid Code.

Where the EU Code User is required to facilitate a generator intertrip function on plant belonging to an Embedded Generator, the EU Code User shall include all information in accordance with those provisions within Appendix F4 and include all relevant information within Schedule 1 of Appendix F4.

The EU Code User shall install and maintain the interface to the intertripping facility such that, on receipt of an appropriate signal(s) from the Transmission System, the selected Embedded Power Station will trip within [XXXX]ms (time to be determined by TO studies) by opening the appropriate EU Code User’s circuit breakers to ensure the Active Power Output of the Embedded Generator is reduced to zero MW.

The EU Code User shall install selection facilities to switch the intertrip scheme into and out of service.

The EU Code User agrees that The Company shall, in operational timescales, issue an Ancillary Services instruction to the Embedded Generator for the arming of the intertrip facility in respect of the [XXXX] (name of power station) pursuant to the Grid Code BC2.8 and CUSC 4.2A. The Embedded Generator [XXXX] shall then instruct the EU Code User to switch the intertrip into service. (amend this paragraph if alternative arrangements have been specified in the TOCO.)

Upon instruction from the Embedded Generator [XXXX] (following an instruction from The Company), The EU Code User is required to switch the intertrip into service for the scenarios defined in Schedule 1. Note: Where this section is not required but in order to retain the ability to include this section in the future, the Power System Engineer should deleted the above paragraphs and state “None identified at this time however the…” and include the paragraph below.

General

The EU Code User shall co-operate with The Company and the Relevant Transmission Licensee in enhancing/amending these facilities, should The Company require this at a later date, and will not unreasonably withhold its agreement to any such proposals.

Except where CUSC 4.2A.6 applies, any such changes of this Appendix F3 and/or to The Company’s and/or the EU Code User’s obligations in respect therefore shall be subject to the provisions of Paragraph 2.9.3 of the CUSC.

- Special Automated Facilities

| Requirement |  |
| --- | --- |
| Transmission System to Demand Intertripping Scheme | Not applicable (unless specified) |
| Transmission System to Directly Connected Customers Intertripping Schemes | Not applicable (unless specified) |

- Other Facilities

| Control Requirements |  |
| --- | --- |
| Automatic Open/ Closure Schemes | Not applicable (unless specified) |
| System Splitting/Islanding Schemes | Not applicable (unless specified) |
| Any control requirements shall be in accordance with the requirements of ECC.6.2.3.8 and ECC.6.2.3.9 | ECC.6.2.3.8 ECC.6.2.3.9 |

Note: these are generally not applicable but may be required for example to manage fault level restrictions or to enable automatic post fault switching.

- Active Network Management Scheme (check for ANMs in this GSP)

(Note- This requirement may or may not be required depending on the connection topology.  For further advice contact the SO Network Capability - GB System Operability Team)

NOTE:- This section is for DNO agreements only, delete if a traction, DSB and non-embedded

This Active Network Management Scheme (ANM) is required to limit the real and reactive power flow at [XXXX]kV substation following faults on the National Electricity Transmission System.

Where the EU Code User is required to provide an ANM facility, the EU Code User shall include all information in accordance to those provisions within Appendix F4 and include all relevant information within Schedule 1 of Appendix F4.

The EU Code User agrees that The Company shall, in operational timescales issue an instruction for the arming of the ANM facility. The Company shall arm the ANM scheme for one or more of the outage combinations as specified in Schedule 1 of Appendix F3.

The EU Code User shall install equipment that will accept signals from the Relevant Transmission Licensee’s marshalling cubicles at [XXXX]kV substation such that upon receipt of a signal by The Company, the total MW and MVAr export at [XXXX]kV substation shall be reduced to a defined export value.  This defined export value will be notified by The Company to the EU Code User either when the scheme is armed or as Transmission System conditions change. In any event, the defined export value will be notified to the EU Code User during pre-fault conditions.

The EU Code User shall install and maintain an ANM facility such that, on receipt of an appropriate signal(s) from The Company, the EU Code User shall reduce the total MW and MVAr export at [XXXX]kV substation within 10s. This shall form part of the EU Code User System.

The ANM scheme will be monitored to ensure it is healthy at all times and provide indications to The Company.  The functionality, performance, availability, accuracy, dependability, security and repair times of the communications links, trip facilities and monitoring facilities provided by the EU Code User from the Relevant Transmission Licensee’s marshalling cubicles located in [XXXX]kV substation to the EU Code User’s interface shall be agreed with The Company at least 24 months before the Completion Date..  (if quicker connection then this should be flexible on a case by case basis please refer to the J)

In the event that the ANM is not healthy, The Company shall instruct the course of action to be taken. In the worst case, the EU Code User may be required to reduce the MW and MVAr export capacity at [XXXX]kV substation as required by The Company.

No single hardware, software, system, communication, interface or power supply failure or depletion of facility shall result in failure to trip within the specified time or an incorrect control action.

The EU Code User shall install isolation facilities to locally switch the ANM facility out of service.  The EU Code User shall not isolate the intertripping facility unless otherwise agreed with the Company.

For the avoidance of doubt, the Relevant Transmission Licensee will provide the necessary signals at the marshalling cubicle within [XXXX]kV substation. The EU Code User is responsible for the installation and maintenance of the cabling between the marshalling cubicle and the EU Code User’s interface equipment. (if not ANM is identified then same comment for the following schemes)

- SGT Reverse Power Flow Control Scheme

NOTE:- This section is for DNO agreements only, delete if a traction, DSB and non-embedded

In order to protect the Relevant Transmission Licensee’s Supergrid Transformers (SGTs) from the risk of trip as a result of excessive overloads from the Embedded Generation installed within the [XXXX] group, the EU Code User is required to design, own, operate and install an SGT Reverse Power Flow Control Scheme (referred to in this technical appendix as “the Scheme”).  The Scheme will be required to control the pre-fault loading on the Grid Supply Point as well as provide the means in effect to intertrip embedded generation in the case of an SGT fault.

It is the EU Code User’s responsibility to design the SGT Reverse Power Flow Control Scheme to manage the embedded generation levels such that the total export limit at [XXXX]kV Substation is limited to the values defined in Schedule 2 of Appendix F3 under both intact and planned outage conditions. The scheme must be permanently armed and meet the following requirements.

Use text below only if the scheme capability is specifying time dependant values:

The EU Code User shall ensure that the Scheme is capable of maintaining the pre-fault loading on each of the SGTs [XXXX] kV Substation within the limits specified by The Company as detailed in Schedule 2 of Appendix F3.  In addition, the EU Code User’s scheme shall ensure that the post fault export across each of the SGTs at [XXXX]kV Substation remain in the time dependant values specified in Schedule 2 of Appendix F3 and are reduced to the post fault steady state values specified in Schedule 2 of Appendix F3 within the time specified in the table. The EU Code User may choose to use either the short term overload values specified in column 3 or column 4 of Schedule 2 of Appendix F3, but it is not permissible to use both in succession. This shall form part of the EU Code User System.

For simplified table delete the above paragraph and use this instead

The Scheme will be monitored to ensure it is healthy at all times.  The EU Code User shall inform The Company and the Relevant Transmission Licensee of any issues related to the scheme that impact on the operation of the Transmission System.  In the event that the scheme is not healthy, the EU Code User will take measures to ensure the Connection Asset Reverse Power Limit defined in Appendix G Schedule 1 part 5 is met.

The Relevant Transmission Licensee will provide the necessary SGT signals (CT, VT and plant status) at a marshalling cubicle within [XXXX] kV substation (ie the Grid Supply Point).

The EU Code User shall be responsible for taking these signals from the Grid Supply Point to the EU Code User’s Scheme.  Any additional equipment required to adapt the above signals to the EU Code User’s scheme requirements shall be supplied, installed, commissioned and maintained by the EU Code User.

The scheme and associated interface engineering shall be jointly agreed between The Company, the Relevant Transmission Licensee, and the EU Code User at least [XXXX] months before the Completion Date (Stage 1).

The EU Code User shall demonstrate the suitability of the scheme to The Company through engagement at the detailed design phase, factory tests and on site performance validation tests.  The requirements shall be agreed with The Company at least [XXXX] months before the Completion Date (Stage 1).  In addition, the EU Code User is also required to supply the additional information as detailed below for agreement with The Company and the Relevant Transmission Licensee at least [XXXX] months before the Completion Date (Stage 1).

The EU Code User shall be responsible for the installation, maintenance and overall costs of the Scheme.

For the avoidance of doubt this scheme does not and will not replace the existing SGT Transformer protection.

Note: Where this section is not required but in order to retain the ability to include this section in the future, the Power System Engineer should deleted the above paragraphs and state “None identified at this time however the…” and include the paragraph below.

General

The EU Code User shall co-operate with the Relevant Transmission Licensee and/or The Company in enhancing/amending these facilities, should the Relevant Transmission Licensee and/or The Company require this at a later date, and will not unreasonably withhold its agreement to any such proposals.

SGT Reverse Power Flow Control Design Settings

As part of the design of the SGT Reverse Power Flow Control Scheme the EU Code User is required to provide The Company and the Relevant Transmission Licensee with details of the following:-

- SGT overload response profiles

- Automatic response times

- Deload / trip Settings

- Failure detection times

- Number of preselected de-load settings

- Additional information as may reasonably be required by The Company and the Relevant Transmission Licensee during the detailed design phase.

The above information is required to be submitted by the EU Code User and supplied to The Company and the Relevant Transmission Licensee as part of the Compliance Process at least [XXXX] months before the Completion Date (Stage 1).

- Synchronising

(ECC.6.2.3.10)

(England and Wales)

NOTE:- Where National Grid owns the LV busbars, use the following paragraph and delete all others.

In addition to the requirements of ECC.6.2.3.10 the EU Code User will be required to provide measurement of the voltage on the EU Code User’s incoming feeders (on circuits where there is a possibility of back feed) to the Relevant Transmission Licensee’s voltage selection scheme in accordance with TS.3.24.60_RES.

NOTE:- Where National Grid does not own the LV busbars, delete other paragraphs and use the following:

In addition to the requirements of ECC.6.2.3.10 the EU Code User will be required to provide measurement of the busbar voltage references in accordance with TS.3.24.60_RES via a voltage selection scheme to enable the Relevant Transmission Licensee to carry out synchronising of its circuits.  The Relevant Transmission Licensee will also contribute to the EU Code User’s voltage selection scheme.

(Scotland) NOTE:- for all Scottish demand agreements use the following paragraph.

In addition to the requirements of ECC.6.2.3.10 the EU Code User will be required to provide measurement of the busbar voltage in accordance with the SPTS/SHETS as part of the synchronising facility, and for use as part of the Automatic Control Scheme employed on the transformer circuits (where such a facility is installed).

There is no requirement for a synchronising facility between the Embedded Generator and the Transmission System. (this para for BELLAs only)

For traction agreements, use the following paragraph and delete all others, if there is a possibility of a back feed further information should be sought from Asset Engineering/Core Construction:

In addition to the requirements of ECC.6.2.3.10, the EU Code User shall ensure that an interlocking scheme is provided to prevent the risk of back feeding the National Electricity Transmission System.

NOTE:- For a DSB/non-embedded customer, delete the above paragraphs and use the following (this assumes the User owns the busbar):

In addition to the requirements of ECC.6.2.3.10, the EU Code User will be required to provide measurement of the busbar voltage in accordance with TS.3.24.60_RES/SPTS/SHETS as part of the synchronising facility. The details of such an arrangement will be discussed and agreed in the detailed design phase.  This will be no longer than 12 months before the Completion Date (Stage 1).

- Automatic Voltage Control

Not applicable for BELLAs, and for traction agreements, in most traction agreements it is likely that a HV ATCC will be specified and no User requirement will be necessary. The exception to this rule would be in the event of a non-standard ownership or connection agreement (eg where the owner owns the Transformer). This should be advised by the relevant TO.

Not less than 3 months before the Commissioning Programme Commencement Date for the agreed works, the EU Code User will agree settings for the Automatic Tap Change Control (ATCC) with The Company and Relevant Transmission Licensee.  Any subsequent alterations to the ATCC settings shall be agreed between The Company, the Relevant Transmission Licensee and the EU Code User.

It is envisaged that the new SGT(s) will be integrated into the existing SGT Automatic Voltage Control System. (this para where applicable)

The EU Code User must also provide switchgear status relevant to busbar topology and voltage references to The Company and Relevant Transmission Licensee to enable The Company in coordination with the Relevant Transmission Licensee to implement ATCC to control the 132kV/66kV/33kV/11kV busbar voltage.  (this para E&W DNO only and not relevant if NG owns the 132kV busbar (unless specified in the TOCO))

(Select voltage based on point of connection)

Appendix F3 - Schedule 1 (delete if not required)

Site Specific Technical Conditions – Circuits to be selected for the Active Network Management Scheme

| Condition | System Maintenance Condition | Trip Condition | Overload condition |
| --- | --- | --- | --- |
| 1 |  |  |  |
| 2 |  |  |  |

or

| Selection | Circuit Name |
| --- | --- |

Appendix F3 – Schedule 2 - SGT Reverse Power Flow Control – GSP Limits

Current GSP limits at [XXXX] kV substation.

Note: TOCO will advise which table. Below table only if the scheme capability is specifying time dependant values.

| System Conditions | Allowed Export Limits |  |  |  |
| --- | --- | --- | --- | --- |
|  | Intact Prefault Loading Condition (MVA) | Maximum Post Fault Loading Condition for 5 Seconds (MVA) | Maximum Post Fault Loading for 30 Seconds (MVA) | Maximum Post Fault Loading Condition Steady State (MVA) |

Insert as many combinations as required to cater for all eventualities.  For further advice consult the SO Network Capability - GB System Operability Team

| System Conditions | Allowed Export Limits |  |
| --- | --- | --- |
|  | Intact Pre-fault loading Conditions (MVA) | Maximum Post fault loading Conditions (MVA) |
| (add example) |  |  |

APPENDIX F4

SITE SPECIFIC TECHNICAL CONDITIONS

RELAY SETTINGS & PROTECTION

| User: | [XXXX] |
| --- | --- |
| Type of User | EU Code User |
| Connection Site: | [XXXX] |

Relay Settings & Protection

The TO must ensure that any requirements for protection are consistent with the Design Specification Investment Proposal and checked by construction or the relevant TO.

- Relay Settings

(ECC.6.2.3.4, ECC.6.2.3.6, ECC.6.2.3.7)

The EU Code User shall complete the attached blank protection schedule pro-forma (Schedule 1 of this Appendix). The EU Code User shall submit the protection coordination report and settings on its plant for agreement with The Company and the Relevant Transmission Licensee. This shall include details of the following:

- Circuit diagrams of both ac connections and tripping for the purposes of interpreting the schedule.

- Protection co-ordination report confirming compliance with the applicable clauses of the Grid Code Connection Conditions. The report shall also show how co-ordination with the Transmission Owner’s existing system backup protection is achieved including proposed back-up protection grading curves.

- Details of the Protection Dependability Index per protected zone.

Not less than 3 months before the Commissioning Programme Commencement Date (as defined in the CUSC) for the agreed works, the EU Code User shall have agreed the protection settings on the EU Code User’s equipment with The Company and the Relevant Transmission Licensee in accordance with ECC.6.2.3.6.  The Company and the Relevant Transmission Licensee shall then finalise the protection settings on Transmission System equipment, complete the protection schedule with supporting details where necessary, and supply it to the User.

Any subsequent alterations to the protection settings (whether by the EU Code User or The Company or the Relevant Transmission Licensee) shall be agreed between The Company and the EU Code User in accordance with the Grid Code (ECC.6.2.3.4 and ECC.6.2.3.7).

No EU Code User equipment shall be energised until the protection settings have been finalised. The EU Code User shall agree with The Company, and carry out a combined commissioning programme for the protection systems, and generally, to a minimum standard as specified in Transmission Procedure (TP) 106 which is available from the Relevant Transmission Licensee’s Extranet.  Access to the Relevant Transmission Licensee’s Extranet can be requested via email to:- transmission.documentcontrol@nationalgrid.com. / by the Relevant Transmission Licensee.(delete as appropriate)

- Grid Supply Point Protection Arrangements

(ECC 6.2.3.1)

For main protection systems, the fault clearance time (from fault inception to circuit breaker arc extinction) for faults on all the EU Code User’s equipment directly connected to Relevant Transmission Licensee’s Transmission System shall meet the following minimum requirement(s): -

[400kV within 80ms or 275kV within 100ms, or 132kV and below within 120ms]. (will vary depending on connection voltage)

Where intertripping is required to open circuit breakers, the overall fault clearance time shall not be extended by more than 60ms to allow such intertripping to operate. (Only applicable to 400kV and 275kV)

The maximum backup fault clearance time at [400kV or 275kV is 300ms, or 132kV and below is 1.5s]. (will vary depending on connection voltage.)

- Engineering Recommendation P24 (for traction agreements only)

It is proposed that the protection arrangements for the supply point will be generally in accordance with The Company’s application and settings policy PS(T) 063 and (E&W only) Engineering Recommendation P24 “AC Traction Supplies for Network Rail.”

APPENDIX F4 - Schedule 1

PROTECTION AND INTERTRIPPING DETAILS AT THE RELEVANT TRANSMISSION LICENSEE/EU CODE USER INTERFACE

SITE NAME:

CIRCUIT NAME*:

* where a feeder exists between two sites, a separate schedule will be required for each end.

| CIRCUIT BREAKER TO BE OPERATED | PROTECTION |  |  |  |  | SPECIFIED CLEARANCE TIME (See F4 Item 2) | MOST PROBABLE CLEARANCE TIME |  |  |  |  | FAULT SETTING |  | RELAY SETTINGS PLUS COMPONENT VALUES | CT RATIO |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | PROTECTED ZONE | FUNCTION | MAKE | TYPE/ RATING | DEPENDABILITY INDEX |  | PROTN | TRIP RELAY | CB | INTER TRIP | TOTAL | PHASE- PHASE | PHASE- EARTH |  |  |

| EU Code User Representative | Name: |  | Date: |  | Signature: |  |
| --- | --- | --- | --- | --- | --- | --- |
| The Relevant Transmission Licensee’s Representative | Name: |  | Date: |  | Signature: |  |

APPENDIX F5

SITE SPECIFIC TECHNICAL CONDITIONS

OTHER TECHNICAL REQUIREMENTS

| User: | [XXXX] |
| --- | --- |
| Type of User | EU Code User |
| Connection Site: | [XXXX] |

Other Technical Requirements

The EU Code User can gain access to the technical specifications from the Relevant Transmission Licensee’s Extranet website.  Access to the Relevant Transmission Licensee’s Extranet website can be requested via email to:- transmission.documentcontrol@nationalgrid.com. (delete this para if in Scotland)

|  | Criteria | Applies to? Delete this column when finished | Grid Code Ref – EU Code User to comply with: | Obligations |
| --- | --- | --- | --- | --- |
|  | Protection of interconnecting connections | All | ECC 6.2.3.6.1 | Defined as the primary conductors from the current transformer accommodation on the circuit side of the circuit breaker to the Point of Connection. (England and Wales – DNO/DSB/NON-EMBEDDED DEMAND) If National Grid owns the LV busbars, use the following paragraph:- The Relevant Transmission Licensee: The Relevant Transmission Licensee will provide the common and per zone equipment. The Relevant Transmission Licensee will design the protection scheme for the Interconnecting Connections at the new Connection Site once the Construction Programme has commenced. The EU Code User: The EU Code User shall provide two Current Transformer Type ‘PX-B’ cores (unless otherwise agreed), in each of the EU Code User’s bays in accordance with TS 3.02.04_RES. The current transformer accommodation referred to above is exclusively for use by the Relevant Transmission Licensee for the protection of the Interconnecting Connections. In order to provide the required dependability and setting for the protection, the EU Code User will be required to install relays and auxiliary components on its circuits that are compatible with those used by The Relevant Transmission Licensee. If National Grid does not own the LV busbars, use the following paragraph and delete the paragraph above. The Relevant Transmission Licensee: The Relevant Transmission Licensee shall provide two current transformers which shall be compatible with those specified by the EU Code User in the current transformer accommodation referred to above exclusively for use by the EU Code User for the protection of the Interconnecting Connections. The type and specification of the current transformers provided by the Relevant Transmission Licensee shall be discussed with the EU Code User in the detailed design phase. The Relevant Transmission Licensee acknowledges that the requirements and specifications for CTs in respect of the protection systems other than in respect of the Protection of Interconnecting Connections shall be discussed and agreed with the EU Code User in the detailed design phase. (Use text below only if User connects to any equipment within the Relevant Transmission Licensee’s busbar protection zone which is GIS): EU Code User shall provide all necessary alarms and indications with respect to any gas zones that straddle the ownership boundary. For Scottish Agreements (DNO, DSB/NON-EMBEDDED DEMAND) delete the paragraphs above and use these ones: The Relevant Transmission Licensee: Will design the protection scheme for the Interconnecting Connections at the new Connection Site once the Construction Programme has commenced. The EU Code User: The EU Code User will be required to install auxiliary components on its circuits, which are compatible with those used by The Relevant Transmission Licensee In order to provide the required dependability and setting for the protection. Shall provide two Current Transformer Type ‘XB’ cores or otherwise agreed, in accordance with the SPTS/ SHETS, in the current transformer accommodation referred to above, exclusively for use by the Relevant Transmission Licensee for the protection of the Interconnecting Connections. If the connection arrangements are unusual and not clearly defined at the application stage delete the above paragraphs and use the paragraph below as a last resort. For all tractions agreements. The protection of the interconnecting connections is to be agreed with the Relevant Transmission Licensee in the detailed design phase. This shall be agreed at least 12 months before the Completion Date (Stage 1). |
|  | Fault Disconnection Facilities | All, Delete as appropriate | ECC.6.2.3.2 | For DNO, NON-EMBEDDED DEMAND and DSB, and where National Grid owns the LV busbars, use the following paragraph:- The EU Code User: To make provision for the tripping of circuit breakers connected at the Connection Point by the Relevant Transmission Licensee protection systems. Where National Grid does not own the LV busbars, use the following paragraph and delete the paragraph above. The EU Code User: To make provision for tripping of National Electricity Transmission System transformer LV circuit breaker by the EU Code User Protection systems. NOTE:- Where no National Grid circuit breaker is provided at the User’s connection voltage the requirements of CC.6.2.3.2 shall apply. Details of the tripping arrangements will however need to be specified in this Bilateral Agreement. It is recommended that further advice is sought from Construction. If the connection arrangements are unusual and not clearly defined at the application stage delete the above paragraphs and use the paragraph below as a last resort. For all tractions agreements. The requirements for fault disconnection facilities are to be agreed with The Company in the detailed design phase. This shall be agreed at least 12 months before the Completion Date (Stage 1). |
|  | Automatic Switching Equipment | Where automatic re-closure of circuit breakers is required following faults on the User’s system, specify here | ECC.6.2.3.3 | The EU Code User: Not applicable. |
|  | Control Telephony | All, but if DSB intends to submit bids and offers to the market, delete this item and use row 5 instead. | ECC.6.5.2 ECC.6.5.5 | (E&W) Where NGET owns the LV busbars, use the following sentence:- Not applicable – Control Telephony will be supplied by The Company. Where NGET does not own the LV busbars, delete the sentence above and use the paragraph below. The EU Code User shall install either: - A free issue telephone handset supplied by The Company (each on dedicated cores); or - A PSTN telephone. (Scotland) If alternative requirements are specified these will be included in the TOCO and need to be included in this section. In some cases this may not be required as Control Telephony facilities may already be installed at site. The EU Code User shall provide accommodation for either:- - A free issue Transmission Control Telephone and Extension Bell (each on designated cores); - A PSTN Telephone; or - Other free issue Control Telephony as agreed. |
|  | Additional Communication Facilities: Trading Point Electronic Data Transfer (EDT), Control Points and Control Point Electronic Dispatch and Logging (EDL) | Only DSB/ non-embedded wishing to participate in the BM | ECC.6.5.8(a) ECC.7.9 OC.7 BC.2 ECC.6.5.8, ECC.6.5.9 and BC.1.4.1 ECC.6.5.8(b) ECC.6.5.2 | The EU Code User: To fulfil the obligations defined in schedule 2 of this Appendix. |
|  | Operational Metering | All | ECC.6.5.6 | NOTE:- National Grid will supply the CTs and VTs for operational metering purposes. The cost of this equipment will however need to be included in the overall cost of the scheme. The Scheme Team will need to determine the specification of this equipment. (DNO England and Wales use this para) The Relevant Transmission Licensee shall supply Voltage Transformers, Current Transformers and Supergrid LV feed equipment sufficient to accomplish the measurement of MWs, MVArs, Voltage, Current, Frequency, Circuit Breaker and Disconnector status. (DNO Scotland use this para) The EU Code User shall continue to provide the present space and location allocated within the EU Code User’s substation to house the SCADA equipment and provide reasonable access to the facility to allow transmission cable connections into this equipment. The EU Code User shall continue to provide voltage and current measurement outputs and plant status indications and alarms to the Transmission SCADA interface equipment. The EU Code User’s substation circuit breaker and disconnector positions are required for the bus section circuit. For DSB, non-embedded demand and traction agreements delete the above and use the below The EU Code User: To fulfil the obligations defined in schedule 1 of this Appendix including the requirements of TS3.24.100_RES. (for SHE-T offers only add text below) The EU Code User can pass “Operational Metering” data through the SHET SCADA System onto The Company. There are two methods of doing this: - Hardwiring signals from the EU Code Users plant to an interface marshalling cubicle/panel – location to be agreed by SHET. The signals will then interface to an SSE RTU or BCU (Bay Control Unit). Where hardwired signals are proposed it is critical that signals are agreed between the EU Code User and The Company at least 1 year before the completion date (stage 1) - A serial DNP3 link to the SHET SCADA System Hardwired interfaces are preferred for small signal counts. Hardwired interfaces shall not be used where substation earth mats are not connected together. In these situations fibre optic cables shall be installed by the EU Code User and interface to the SHET substation. The exact details shall be agreed with SHET at the detailed design stage and all fibre optic cables shall be installed to SHET specifications. The exact demarcation points shall be agreed but typically the fibre will terminate in a suitably sited ”meet me” chamber external to the SHET substation with adjacent vehicular access. Any method of signal exchange shall be agreed by SHET at least 1 year before the completion date (stage 1). Exact details of the DNP3 link shall be agreed with SHET at the design stage. The EU Code User equipment and interface shall conform to the SHET equipment. This shall include both DNP3 protocol implementations and fibre optic cables and fibre optic serial interface devices (where fibre optic is used). This shall require detailed information exchange in advance (at least 1 year) between the EU Code User and SHET regarding proposed equipment and DNP3 protocol implementation. It shall also require successful testing of the proposed interface and equipment during a Factory Acceptance Test and further Site Acceptance Testing prior to on-site commissioning. Any DNP3 link shall comply with IEEE 1815-2012 -- IEEE Standard for Electric Power Systems Communications-Distributed Network Protocol (DNP3) Any EU Code User systems which comprise Redundant DNP3 systems shall require special measures to ensure that only one system responds at any time and DNP3 event queues are synchronised between systems. Further information is available on request from SHET. The EU Code User: (delete the above and use this text if embedded – SHE-T only) To be agreed between the EU Code User and host Distribution Network Operator. |
|  | Voltage Phase Unbalance | Traction, non-embedded demand and DSB agreements only for Scottish agreements the information will be provided by the Scottish TO in the TOCO. | ECC6.1.5(b) ECC6.1.6 | (For DSB/NON-EMBEDDED DEMAND) The EU Code User: To provide Voltage Unbalance Assessment information as specified in PC.4.4.1, PC.4.4.2, PC.4.5, PC.A.4.7 and DRC.6.1.5 Schedule 5, of the Grid Code. The Relevant Transmission Licensee: To carry out voltage unbalance assessment in accordance with ECC.6.1.5(b) and ECC.6.1.6. Following the assessment, the Relevant Transmission Licensee will (where applicable) specify to the EU Code User (by written notice), the negative phase sequence current limits and phase allocations (as appropriate) to which The EU Code User will comply. (For traction agreements, delete above paras and use this) The EU Code User: To contain the voltage phase unbalance NPS voltage level at XXXX kV Substation to within the limits specified in sections ECC.6.1.5 and ECC.6.1.6 of the Grid Code (and the NPS voltage limits set out in the Addendum to Engineering Recommendation P24 – Scotland only), the traction demand connected to XXXX kV Substation shall be limited to: Intact (N-0): Feeder F1; Feeder F2. 10-minute average: XX MVA 30-minute average: XX MVA; 10-minute average: XX MVA 30-minute average: XX MVA. Loss of Feeder 1: Feeder F1; Feeder F2. 10-minute average: XX MVA 30-minute average: XX MVA; 10-minute average: XX MVA 30-minute average: XX MVA. Loss of Feeder 2: Feeder F1; Feeder F2. 10-minute average: XX MVA 30-minute average: XX MVA; 10-minute average: XX MVA 30-minute average: XX MVA. (additional loading scenarios and load restrictions may be added as required and agreed with User/Customer) Relevant Transmission Licensee To specify which phases are to be used If the supply is to be taken from a single phase or from a phase-to-phase connection. |
|  | AC System Voltage Variations | All | ECC.6.1.4 | (E&W use the top 2 paragraphs, and delete the 1 at the bottom:) The EU Code User: In addition to withstanding the requirements of ECC.6.1.4 of the Grid Code, the EU Code User’s plant and apparatus shall also be capable of withstanding typical fundamental frequency temporary overvoltages that may occur on the onshore transmission system and should not produce, by means of their equipment switching or otherwise, TOVs exceeding the limits stated in the TGN (E)288 – (version at date of offer signature) which is available from the Relevant Transmission Licensee upon request. Detailed requirements in relation to this study can be agreed with the Relevant Transmission Licensee at a time convenient to the EU Code User. The results of this study must be provided to the Relevant Transmission Licensee by the date defined in the Appendix J. (Scotland delete the above and use the following:) The EU Code User: In addition to withstanding the requirements of ECC.6.1.4 of the Grid Code, the EU Code User’s plant and apparatus shall also be capable of withstanding typical fundamental frequency temporary overvoltages that may occur on the onshore transmission system. |
|  | Voltage Waveform Quality | Traction, data centre or power electronic load agreements only | ECC.6.1.5 ECC.6.1.6 ECC.6.1.7 | The EU Code User: In order to limit voltage change at the EU Grid Supply Point, (for example during energisation), the EU Code User shall be required to satisfy the requirements of ECC.6.1.7(a) of the Grid Code. The EU Code User will take appropriate measures to minimise the probability and severity of electromagnetic voltage transients which may occur when the EU Code User (or any material subsystem) is connected to or disconnected from the National Electricity Transmission System. The EU Code User will provide the Relevant Transmission Licensee with details of such measures and an assessment of the predicted probability and severity of such transients. In the event that the Relevant Transmission Licensee needs to undertake transient overvoltage assessments, the EU Code User will be required to provide the data required under PC.A.6.2.1. In accordance with ECC.6.1.7(b), following the voltage fluctuation assessment, the Relevant Transmission Licensee shall specify to the EU Code User (by written notice) the flicker limits. The EU Code User shall ensure that: - The total repetitive voltage changes (flicker) due to the operation of the EU Code User’s equipment, when aggregated with existing flicker levels, do not exceed these values; and that - Any inter-harmonic component produced by the EU Code User’s equipment shall be limited to a magnitude where the magnitude of any resultant beat frequency between this and the adjacent harmonic frequency remain within the specified limit for Pst. The EU Code User will provide the Relevant Transmission Licensee with details of an assessment showing compliance with the flicker limits. |
|  | Demand Reduction | All | OC.6.6 ECC.6.4.3 | The EU Code User: Is required to make arrangements (specified in OC.6.6 and ECC.6.4.3) that will enable automatic low frequency demand disconnection to limit the consequences of a major loss of generation or an event which leaves part of the system with a generation deficit. To discuss and agree (as applicable) the arrangements and settings with The Company in the detailed design phase which shall be at least 18 months before the Completion Date unless otherwise agreed. (use this para for E&W traction and DSB / non-embedded customers) |
|  | Power Quality Monitoring | Traction, non-embedded customers or power electronic load agreements only NB Scottish TOs will define any need for PQM in the TOCO, if none then put Not applicable |  | The Relevant Transmission Licensee/EU Code User: (depending on who owns the transducer) To provide three phase voltage transducers of suitable accuracy and these shall be appropriately sited at [XXXX]kV substation to enable continuous power quality voltage monitoring to be undertaken whether or not the EU Code User’s System is energised. Voltage transducers shall be of Capacitor Voltage (CVT) type. The CVT shall be equipped with high current CT (HCCT) and low current CT (LCCT). Primary windings of HCCT and LCCT shall be connected to earth connections of the low voltage capacitor unit and electromagnetic unit (EMU), respectively. The secondary wiring of HCCT and LCCT shall be connected via cable to a separate terminal box which houses the signal conditioning module (SCM). This electronic module converts the signals to an output suitable for Quality of Supply Measurements. To also provide three phase current transducers of suitable accuracy on the higher voltage side of the [400/25-0-25kV] transformers (traction only) at the [XXXX]kV substation to enable continuous power quality current monitoring to be undertaken. (A current transducer would be suitable for power quality monitoring if it is also compliant with International Standard IEC 61869-2 “Requirements for protective current transformers for transient performance.”) The transducers would be required to meet TS 3.02.04_RES “Current Transformers for Protection and General Use.” The output signal of these voltage and current transducers shall be provided to the Relevant Transmission Licensee. (only if EU Code User owned) To provide cubicle space, power supplies and associated ancillary equipment and install permanent, Class A power quality monitors as defined in IEC 61000-4-30 at the Grid Supply Point in order to check compliance against specific limits. (delete the following first paragraph if traction load and if NGET owns the transducers): To provide signals from the voltage and current transducers (as specified above) to a suitable termination point within the cubicle. For information, the Relevant Transmission Licensee will undertake a minimum of four weeks of continuous power quality voltage measurements using the above facilities immediately prior to the energisation of the EU Code User’s feeders to establish a baseline for compliance with the Grid Code. Continuous power quality monitoring will then be performed during and after commissioning. The current transducers in each EU Code User’s feeder shall be sited such that the monitored currents include any contribution from reactive power compensation and/or harmonic mitigation equipment. (traction only) |
|  | Harmonic Content | Traction, DSB, data centre or power electronic load (including electrolysers)agreements only | ECC.6.1.5(a) | The EU Code User: Shall provide The Company and Relevant Transmission Licensee with Harmonic Assessment information (as specified in PC.4.4.1, PC.4.4.2, PC.4.5, PC.A.4.7, DRC.6.1.5 Schedule 5, DRC.6.1.7 Schedule 7 of the Grid Code) so that the Relevant Transmission Licensee can carry out an harmonic voltage distortion assessment in accordance with Grid Code Conditions ECC.6.1.5(a). If regenerative braking is to be employed, this shall be explicitly stated in the Harmonic Assessment information and the effect of it shall be included in the data provided to The Company and Relevant Transmission Licensee. (this para for traction agreements only) The Company (upon advice from the Relevant Transmission Licensee): Following the above assessment, will specify to the EU Code User (by written notice), the harmonic voltage distortion or harmonic current emission limits (as appropriate). The EU Code User shall comply with the above limits. The specification of the above limits will normally be calculated using the data provided by the EU Code User. If the EU Code User subsequently notifies The Company (who in turn will notify the Relevant Transmission Licensee) of any changes to this data, The Company (upon advice from the Relevant Transmission Licensee) reserves the right to amend the limits and to issue revised limits to the EU Code User following any revised Voltage Waveform Quality Assessment. (delete this para if it is a Scottish agreement) |
|  | Load Characteristics at the Grid Supply Point | DNO and data centres or power electronic load agreements only |  | The Relevant Transmission Licensee in coordination with The Company: Reserves the right to conduct detailed demand assessments on the [XXXX] kV substation load and offer advice on any special measures required. The Relevant Transmission Licensee does not envisage the need to undertake such an assessment but will monitor the connection point load characteristics through Technical Planning Meetings and any other means available. (for E&W DNO agreements only, use the following para) Power Factor: To ensure the network can be operated within statutory voltage limits, The Company will from time to time compare historic MW and MVAr flow data at the GSP interface across a year of operation with the EU Code User’s week 24 submission. Where a discrepancy exists the EU Code User will co-operate with The Company and the Relevant Transmission Licensee to satisfactory resolve any resulting operational compliance issues. |
|  | Reactive Capability Limits | Applicable only to Non-Embedded Customers and totally new Distribution Systems who are classified as EU Code Users with EU Grid Supply Points | ECC.6.4.5 | The EU Code User at its EU Grid Supply Point is required to satisfy the requirements of ECC.6.4.5. (Note – Where there is a requirement for specific reactive capability limits these need to be specified in this section but will need to be justified and agreed with the EU Code User). |
|  | Reactive Capability Limits | Existing Scottish DNO agreements only |  | In order to prevent the risk of high or low voltages occurring at [XXXX]kV substation and on adjacent [XXXX]kV Transmission circuits, the EU Code User shall be required to ensure that the connection of any Embedded Generation within the Network Operator’s System does not increase the current levels of reactive power exported or imported to [XXXX]kV substation beyond a maximum of +/-[XXXX]MVArs. (only to be used if there is a risk of high or low system volts as a result of the uncontrolled spill of MVArs from a DNO connection point |
|  | Paralleling | Direct Connect only, all but DNO agreements |  | The EU Code User: To ensure there is no paralleling of The National Electricity Transmission System through the EU Code User’s System. |
|  | Safety and Operational Interlocking | All |  | The EU Code User: Electrical and mechanical interlocking to be provided by the EU Code User in accordance with TS.3.01.01_RES/SPTS/SHETS. Scottish TOs will define in the TOCO, if not use this text |
|  | Earthing Facility | All |  | (For DNO, non-embedded demand and DSB) The Relevant Transmission Licensee: (DNO, non-embedded demand and DSB, delete this para if a traction agreement) Will provide at least two points within its substation(s) to facilitate any bonding with the EU Code User’s site if required. All earth mats on the EU Code User site(s) and the Relevant Transmission Licensee’s site(s) where these are adjacent may be bonded together. The Relevant Transmission Licensee’s site earth mats can be bonded to the EU Code User’s site earth mat. (next 3 paras for traction agreements only) At this stage the earthing system appropriate to the Relevant Transmission Licensee and the EU Code User sites has not been fully established. The Relevant Transmission Licensee’s site earth mat would be expected in this instance to be bonded to the EU Code User’s site earth mat, excepting any equipment that the EU Code User installs at the Relevant Transmission Licensee’s site at [XXXX] kV substation. The Relevant Transmission Licensee can provide at least two points within its substation(s) to facilitate any bonding should this be required. Should the EU Code User’s site not be bonded to the Relevant Transmission Licensee’s Earthing mat, then the Earthing requirements will need to be discussed and agreed with The Company and Relevant Transmission Licensee in the detailed design phase. The earthing arrangements of the EU Code User’s [XXXX] kV Substation shall comply with ENA ER P24 (section 11) and an agreement of the connections between the Relevant Transmission Licensee’s substation earthing system and the supply return conductor side of the 25kV winding of the 400/25kV transformers shall also be finalised and agreed in the detailed design phase. (All) The EU Code User: To carry out an earthing survey of their sites prior to construction of the EU Code User’s Plant and Apparatus. The earthing system is to be designed to withstand a short circuit current of [XX kA for YY seconds]. (63 kA for 1 second at 400 kV substations, 40kA for 1 second at 275 kV substations and 40kA for 3 seconds at 132 kV substations) (Note this will depend on connection voltage and TO area). [132kV 40kA for 3sec, 66kV 31.5kA for 3 secs, 33kV 31.5kA for 1sec, 25kV 10kA for 1sec] The EU Code User shall ensure that it’s Plant and Apparatus is designed and installed such that the rise of earth potential (ROEP) at [XXXX] kV substation conforms to the touch, step and transfer voltage limits which are defined in ENA TS 41 – 24. Where intertripping (second main protection) is required to open circuit breakers, the overall fault clearance time shall not be more than [XX]ms at [XXX]kV substations. (180ms at 132 or 66 kV) The EU Code User’s earthing system design review shall take the Relevant Transmission Licensee’s earthing system design into account and the EU Code User shall collaborate with the Relevant Transmission Licensee to ensure that compliance has been demonstrated at the Grid Supply Point which also mitigates 3rd party impact as required. The earthing system at [XXXX] kV substation shall be designed to comply with ESQCR 2002 and BS EN50522. |
|  | Settlement Metering | For DNO, new templates only and DSB, non-embedded demand or traction agreement, | ECC.6.2.2.3.5 | (Where the Relevant Transmission Licensee are providing the settlement metering use this.) The Relevant Transmission Licensee: To provide CTs/VTs that comply with the relevant metering Code of Practice required for Settlement. To provide the Settlement Meters. All of the above to be completed prior to energisation and in accordance with the Balancing and Settlement Code (BSC). The EU Code User: Shall be responsible for registering compliant items of Metering Equipment for Settlement purposes, in accordance with the BSC and related procedures, with the relevant timescales and prior to energisation of the circuit. The EU Code User shall ensure that the Settlement Metering shall be compatible with all interfacing equipment installed by the Relevant Transmission Licensee at [XXX] kV substation. (Where the EU Code User are providing the settlement metering delete the above and use the following.) The EU Code User: To provide CTs/VTs that comply with the relevant metering Code of Practice required for Settlement. To provide the Settlement Meters and register compliant items of Metering Equipment for Settlement purposes. All of the above to be completed prior to energisation and in accordance with the Balancing and Settlement Code (BSC). |
|  | Voltage Regulation at the Grid Supply Point | Only for DNO agreements with Embedded generation where a statement of works process has been instigated **!Ensure that the DNO is in agreement before adding this item!** |  | The EU Code User should be aware that Embedded Large and Embedded Medium Power Stations are required to satisfy the reactive capability and voltage control requirements of ECC.6.3.2, ECC.6.3.8 Grid Code. For Small Embedded Power Stations as defined in Appendix G Parts 2, 3 and 4 of this Connection Agreement, the EU Code User shall ensure that each Generating Unit or Power Park Module within each Embedded Small Power Station shall have a reactive capability of between 0.95 Power Factor Lead to 0.95 Power Factor Lag at Rated MW Output at the EU Code User System Entry Point. Subject to the provisions of 11.2.2 of this Connection Agreement, during the operational timeframe, the EU Code User shall instruct each Generating Unit or Power Park Module within each Embedded Small Power Station of its required operating Power Factor which shall be within the capability range of each Embedded Small Power Station defined in Appendix G Parts 2, 3 and 4 of this Connection Agreement. There is no restriction on the EU Code User if they wish to employ an alternative method to manage MVAr transfers at the Grid Supply Point, for example through the installation of reactive compensation equipment, intertripping Embedded Generation or the application of other suitable control schemes. |
|  | Emergency Instructions | Only for DNO agreements with Embedded generation where a statement of works process has been instigated **!Ensure that the DNO is in agreement before adding this item!** |  | In accordance with the requirements of BC2.9.1.4, using the principles set out in OC6.7.1 the EU Code User shall maintain a facility such that under emergency conditions on the National Electricity Transmission System, the EU Code User shall have the ability to de-energise the Embedded Generation detailed in section 11.3 and Appendix G Parts 2, 3 and 4 of this Connection Agreement, upon instruction from The Company. |
|  | Compliance Testing | All | ECP | The EU Code User: To demonstrate compliance with the requirements of the Grid Code. |
|  | Electromagnetic Transients, Voltage Fluctuations and Transformer Energisation | Traction, DSB and non-embedded only | ECC.6.1.7 (a) ECC.6.1.7 (b) | The EU Code User: To minimise the probability and severity of electromagnetic voltage transients or transformer inrush at the Grid Entry Point which may occur when the EU Code User's Plant and Apparatus or any material subsystem is connected to or disconnected from the National Electricity Transmission System, the EU Code User shall provide The Company (for onward transmission to the Relevant Transmission Licensee) with details of such measures and an assessment of the predicted probability and severity of such transients or transformer inrush. In the event that The Company/Relevant Transmission Licensee needs to undertake transient overvoltage assessments or voltage assessment studies, the EU Code User will be required to provide the data required under PC.A.6.2.1 or PC.A.6.5 of the Grid Code. |
|  | Flicker | Traction and all power electronic based non-embedded customers/DSB |  | The EU Code User: To follow EREC P28-Issue 2 and provide a report to show – considering time-variation of frequency – that their flicker impact is compliant with Stage 2 assessment criteria of EREC P28-Issue 2. If the Stage 2 assessment criteria cannot be satisfied then The Company (upon advice from the Relevant Transmission Licensee) shall issue appropriate limits in accordance with Stage 3 assessment procedure within EREC P28-Issue 2. |
|  | RMS Model Requirement | Non-embedded customers except traction | PC.A.9 | The EU Code User: Is required to satisfy the requirements of PC.A.9. Please note the following: PowerFactory RMS model(s): This includes model(s) and any associated set up script(s) that form part of the model delivery to The Company and should be compliant with PC.A.5 and PC.A.9. Any set up scripts should be compatible with the PowerFactory network used by The Company. Also, the RMS model shall be capable of operating with sufficient accuracy at an integration time step of 10ms. PowerFactory version: Model(s) to be delivered in a version of PowerFactory to be agreed with The Company. After the PowerFactory model is provided, the model validation report which compares results against simulation results of the PowerFactory model and FAT results should be submitted. The validation should be carried out at a 10ms integration time step. Specification for the model to be agreed with The Company and Relevant Transmission Licensee of all EU Code User’s plant to enable the following studies: Transient Analysis studies – electromechanical. The model and the validation report will be assessed by The Company and the Relevant Transmission Licensee. An updated version of the model and validation report is required to be submitted to take into account any issues identified by The Company and the Relevant Transmission Licensee and any updates that are identified during commissioning. |
|  | EMT Model Requirement | Non-embedded customers except traction | PC.A.9 | The EU Code User: Is required to provide the detailed EMT model for the EU Code User’s Plant and Apparatus. After the EMT model is provided, the equipment model validation report which compares results against simulation result of EMT model and equipment FAT results should be submitted. PSCAD model(s): This includes model(s) and any associated set up script(s) that form part of the model delivery to The Company and should be compliant with PC.A.9. Any set up scripts should be compatible with the PSCAD network used by The Company. PSCAD version: Specification for the model (including time step) should be agreed in advance between The Company in consultation with Relevant Transmission Licensee and the EU Code User. The model and the validation report will be assessed by The Company and the Relevant Transmission Licensee. An updated version of the model and validation report is required to be submitted to take into account any issues identified by The Company and the Relevant Transmission Licensee and any updates that are identified during commissioning. Please note: A detailed (EMT Encrypted model) is a model having the same source code loaded in the actual plant controllers, which defines the plant control philosophy and logic. Additional guidance on EMT model is also published on The Company website. https://www.neso.energy/industry-information/connections/compliance-process#Compliance-documents Document title: Guidance for EMT Models V2.0 Sep 2025 |
|  | Fault Ride Through | non-embedded customers |  | Fault Ride Through: The EU Code User shall stay connected to the System and remain operable within the frequency ranges and time periods specified below: Frequency Range (Hz); Time Period of Operation (s). 47.0 – 47.5Hz; 60s. 47.5 – 49.0Hz; 90min and 30s. 49.0 – 51.0Hz; Unlimited. 51.0 – 51.5Hz; 90min and 30s. 51.5 – 52Hz; 20min. Faults lasting up to 140ms: The EU Code User is required to remain connected and stable for any balanced and unbalanced fault where the voltage at the Grid Supply Point remains on or above the heavy black line shown in Figure 1. For up to 30 minutes following such a fault event the EU Code User’s Plant and Apparatus is required to remain connected and stable provided System operating conditions have returned within those specified in ECC.6.1 of the Grid Code. The voltage against time curves defined in Figure 1 expresses the lower limit (expressed as the ratio of its actual value and its reference 1pu) of the actual course of the phase to phase voltage (or phase to earth voltage in the case of asymmetrical/unbalanced faults) on the System voltage level at the Grid Entry Point during a symmetrical or asymmetrical/unbalanced fault, as a function of time before, during and after the fault. Figure 1 Voltage Parameters (pu); Time parameters (seconds). Uret; 0; tclear; 0.14. Uclear; 0; trec1; 0.14. Urec1; 0; trec2; 0.14. Urec2; 0.85; trec3; 2.2. In addition:- - the EU Code User’s Plant and Apparatus shall be capable of satisfying the above requirements when operating at Rated MW output and rated Power Factor (both leading and lagging) as applicable. - The Company will specify upon request by the User the pre-fault and post fault short circuit capacity (in MVA) at the Grid Entry Point. - The pre-fault voltage shall be taken to be 1.0pu and the post fault voltage shall not be less than 0.9pu. - To allow a User to model the Fault Ride Through performance of its Plant and Apparatus, The Company will provide additional network data as may reasonably be required by the EU Code User to undertake such study work in accordance with PC.A.8. Alternatively, The Company may provide generic values derived from typical cases. - The Company will publish fault level data under maximum and minimum demand conditions in the Electricity Ten Year Statement. - Each EU Code User shall satisfy the requirements in (i) – (viii) unless the protection schemes and settings for internal electrical faults trips the EU Code User’s Plant and Apparatus. The protection schemes and settings should not jeopardise Fault Ride Through performance. - The undervoltage protection at the Grid Entry Point shall be set by the EU Code User according to the widest possible range, unless The Company and the EU Code User have agreed to narrower settings. All protection settings associated with undervoltage protection shall be agreed between the EU Code User and The Company and Relevant Transmission Licensee’s. - The EU Code User’s Plant and Apparatus shall be designed such that upon clearance of the fault on the Transmission System and within 0.5 seconds of restoration of the voltage at the Grid Entry Point to 90% of nominal voltage or greater, Demand shall be restored to at least 90% of the level immediately before the fault. Once the Demand has been restored to the required level, Active Power oscillations shall be acceptable provided that: - The oscillations are adequately damped. - In the event of power oscillations, The EU Code User’s Plant and Apparatus shall retain steady state stability. Where the EU Code User’s Plant and Apparatus comprises switched reactive compensation equipment (such as mechanically switched capacitors and reactors), such switched reactive compensation equipment shall be controlled such that it is not switched in or out of service during the fault but may act to assist in post fault voltage recovery. Faults lasting over 140ms: In addition to the above requirements the EU Code User shall remain transiently stable and connected to the National Electricity Transmission System without tripping of any Plant and Apparatus for balanced Supergrid Voltage dips and associated durations anywhere on or above the heavy black line shown in the Figure 2 below: Figure 2 In addition, the EU Code User’s Plant and Apparatus shall - Restore its Demand in a linear and proportional manner following Supergrid Voltage dips on the Onshore Transmission System as described in Figure 2 above, within 1 second of restoration of the voltage to 0.9 pu of the nominal voltage at the Onshore Grid Entry Point to at least 90% of the level available immediately before the occurrence of the dip. - Once the Demand has been restored to the required level, any Active Power oscillations are required to be adequately damped. For the avoidance of doubt a balanced Onshore Transmission System Supergrid Voltage meets the requirements of ECC.6.1.5 (b) and ECC.6.1.6 of the Grid Code. - For up to 30 minutes following such a Supergrid Voltage dip on the Onshore Transmission System the EU Code User’s Plant is required to remain connected and stable provided System operating conditions have returned within those specified in ECC.6.1 of the Grid Code. Other Fault Ride Through Requirements - The User’s Plant and Apparatus will be required to withstand, without tripping, the negative phase sequence loading incurred by clearance of a closeup phase-to-phase fault, by System Back-Up Protection on the Onshore Transmission System operating at Supergrid Voltage. - The EU Code User is required to confirm to The Company, their repeated ability to operate through balanced and unbalanced faults and System disturbances each time the voltage at the Grid Entry Point falls outside the limits specified in ECC.6.1.4 of the Grid Code. Demonstration of this capability would be satisfied by the EU Code User supplying the protection settings of their plant, informing The Company of the maximum number of repeated operations that can be performed under such conditions and any limiting factors to repeated operation such as protection or thermal rating; - Notwithstanding the requirements of clause (iv) below, EU Code User’s Plant and Apparatus shall be capable of remaining connected during single phase or three phase auto-reclosures to the National Electricity Transmission System and operating without power reduction as long as the voltage and frequency remain within the limits defined in ECC.6.1.4 and ECC.6.1.2; - For the avoidance of doubt the requirements specified in this section do not apply to the EU Code User’s Plant and Apparatus when connected to either an unhealthy circuit and/or islanded from the Transmission System even for delayed auto reclosure times. |
|  | Frequency Sensitivity | Electrolysers only |  | Limited Frequency Sensitive Mode – Overfrequency (LFSM-O) The EU Code User’s Plant and Apparatus shall be capable of increasing Demand in response to Frequency on the Total System when this rises above 50.4Hz unless the User’s Plant and Apparatus is already operating at its maximum Demand. For the avoidance of doubt, the provision of this increase in Demand is not an Ancillary Service. The EU Code User shall be capable of operating stably during LFSM-O operation. - The rate of change of Demand increase must be at a minimum a rate of 2 percent of demand per 0.1 Hz deviation of System Frequency above 50.4Hz (ie a Droop of 10%) as shown in Figure 3 below. This would not preclude the EU Code User from designing their Plant and Apparatus with a Droop of less than 10% but in all cases the Droop should be 2% or greater. - The increase in Demand must be continuously and linearly proportional, as far as is practicable, to the excess of Frequency above 50.4 Hz and must be provided increasingly with time over the period specified in (iii) below. - As much as possible of the proportional increase in Demand must result from the frequency controller action and must be achieved within 10 seconds of the time of the Frequency increase above 50.4 Hz. The EU Code User’s Plant shall be capable of initiating a power Frequency response with an initial delay that is as short as possible. If the delay exceeds 2 seconds the EU Code User shall justify the variation, providing technical evidence to The Company. - The residue of the proportional increase in Demand which results from automatic action of the EU Code User’s Plant control devices other than the frequency control devices must be achieved within 3 minutes for the time of the Frequency increase above 50.4Hz. - For the avoidance of doubt, the LFSM-O response must be reduced when the Frequency falls again and, when to a value less than 50.4Hz, as much as possible of the reduction in Demand must be achieved within 10 seconds. Figure 3: Pref is the reference Active Power demand to which ΔP is related and ΔP is the change in Active Power demand from the Demand Module. The Demand Module has to increaseActive Power demand with a droop of 10% or less based on Pref. - The EU Code User’s Plant which is providing Limited High Frequency Response (LFSM-O) must continue to provide it until the Frequency has returned to or below 50.4Hz or until otherwise instructed by The Company. - Steady state operation above the EU Code Users Plant and Apparatus above its Maximum Demand is not required. - All reasonable efforts should in the event be made by the EU User to avoid such tripping provided that the System Frequency is below 52Hz. If the System Frequency is at or above 52Hz, the requirement to make all reasonable efforts to avoid tripping does not apply and the EU Code User is required to take action to protect its Plant and Apparatus. Limited Frequency Sensitive Mode – Underfrequency (LFSM-U) The EU Code User’s Plant and Apparatus is required to satisfy the following requirements:- - Be capable of automatically reducing its Demand below 49.5Hz as shown in Figure 4. A typical value of the Droop would be 1% where this does not result in control system instability or plant difficulties. In all cases the Droop shall be between 0.6% and 1.2% and shall be agreed with The Company. - The reduction in shall be continuously and linearly proportional, as far as is practicable, to the reduction in Frequency below 49.5 Hz. - As much as possible of the proportional reduction in Demand must result from the Frequency control device action and must be achieved within 10 seconds of the time of the Frequency decreases below 49.5 Hz. The EU Code User’s Plant shall be capable of initiating a power Frequency response with an initial delay that is as short as possible. Delays that exceed 2 seconds shall be justified by the EU Code User providing technical evidence to The Company and in any event as much as possible of the proportional reduction in Demand shall be achieved within 10 seconds. - If the EU Code User’s Plant has not achieved at least a zero Demand when the System Frequency has reached 48.9Hz, it shall be instantaneously tripped. Where the EU Code User’s Plant trips, it shall not be permitted to reconnect to the System until instructed by The Company in accordance with BC2.5.2. Figure 4: Performance with falling frequency Once the System Frequency starts to rise above the minimum reached, it shall be in accordance with Figure 5 below. For example, point Z denotes the minimum frequency that the Total System reached during a particular low System Frequency event, as the System Frequency starts to rise, the Demand of the EU Code User’s Plant should remain at a constant level until 49.5Hz is reached as denoted by the dashed black lines. Once the System Frequency has risen above 49.5Hz the EU Code Users Plant is permitted to increase Demand so long as it operates above 49.5Hz. Figure 5: Active Power performance with increasing frequency Frequency Sensitive Mode (49.5-50.5Hz operation) If the EU Code User wishes to provide a Demand Response Service this shall be in accordance with the Grid Code Demand Response Services Code. Where such a service is Demand Response Service is provided and agreed with The Company this would be in accordance with the Ancillary Services Agreement. |
|  | Ramping Rates | All non-embedded customers | BC.A.1.1 | The EU Code User: As a BM participant the EU Code User is required to satisfy the Ramp Rate requirements of BC.A.1.1 |
|  | Software Quality Assurance | All |  | The EU Code User: The User must adopt and be able to demonstrate the use of recognised software quality assurance techniques to manage control system design and parameter changes implemented during the commissioning process. This is to demonstrate that the control system undergoing testing remains aligned with the models and simulations submitted for approval by the User at the ION stage. As a minimum, design review and version control techniques should be employed to maintain the integrity and design intent of any software that is undergoing commissioning. A test plan should be submitted to The Company, for information, prior to site commissioning activities taking place. The Company also reserves the right to attend selected site commissioning tests, to witness the effective use of the quality plan and associated procedures, as deemed appropriate. |

Appendix F5 - Schedule 1 (Traction, DSB and non-embedded (eg data centres) only, delete if not)

Site Specific Technical Conditions - Operational Metering (ECC.6.5.6) in respect of The Company and Relevant Transmission Licensee

| Description | Units | Accuracy | Type | Provided by | Notes |
| --- | --- | --- | --- | --- | --- |
| Voltage and Current measurements to be agreed with The Company. | MW MVAr | 1% of meter reading | Signals to have 1 second update rate or better | EU Code User. | The functionality, performance, availability, accuracy, reliability, delivery point, protocol measurement point and repair times of the equipment generating and supplying the signals (ie the meters and communication links) shall be agreed with The Company and the Relevant Transmission Licensee at least 12 months before the Completion Date (Stage 1). Note: The metering of each unit should be independent and should not impact/affect nor be impacted/affected by any other surrounding metering regardless of ownership. EU Code User to provide Single Line Diagram showing location of CT/VT equipment and nomenclature of HV Apparatus. The Company will use this information to notify the EU Code User of which HV circuit breaker and disconnector positions (ie status indications) and measurement points are required . |
| Where relevant, all EU Code Users circuit HV circuit breaker(s) and disconnector(s). | Open/ Closed Indication | N/A | Status Indication | EU Code User. |  |

| Residential units (DFS – demand flexibility service only – delete this table and text line below in red if not) | Range | Scale (Unit) | Accuracy | Resolution | Refresh Rate |
| --- | --- | --- | --- | --- | --- |
| Active Power | -100MW to +100MW | MW | 1% of meter reading | 1MW | 1 per second |
| Reactive Power ** | -100MVar to +100MVar | MVar | 1% of meter reading | 1MVar | 1 per second |
| Circuit Breaker Simulated Indications | Open/Closed | 0/1 | Not Applicable | Not Applicable | On Change |

** If no Reactive Power is available a value of 0MVar needs to be sent

Note: In the event that any part of the EU Code User’s Operational Metering equipment, including the communications links to [XXXX]kV substation fails, then the EU Code User will be required to repair such equipment within 5 working days of notification of the fault from The Company or Relevant Transmission Licensee unless otherwise agreed.

Note: The specifications for Operational Metering are defined in TS3.24.100_RES which is included in the Annex to the General Conditions of the Grid Code which is available on The Company’s website.  Please see reference to the Annex to the General Conditions of the Grid Code on the Useful Links page at the end of this Appendix.

Note:

- All meters should have a latency value of less than or equal to 5s

- The EU Code User is also required to recalibrate operational metering every 5 years.

Appendix F5 - Schedule 2

Site Specific Technical Conditions – Additional Communications Facilities (ECC.6.5)

DELETE THIS ENTIRE SCHEDULE IF ADDITIONAL COMUNICATIONS FACILITIES ARE NOT REQUIRED – DSB or non-embedded demand wishing to participate in the BM agreements only

| Description | Location | Source | Provided By | Comments |
| --- | --- | --- | --- | --- |
| Control Telephone ECC.6.5.2 to ECC.6.5.5, ECC.6.5.8, ECC.6.5.9 and BC.1.4.1 | Control Point | The Transmission Substation Exchange. | The EU Code User to provide and install wiring from the EU Code User’s Control Point to The Company substation exchange and install free issue handset. The Relevant Transmission Licensee to provide communications path to the EU Code User’s Control Point site (Great Britain only) in conjunction with the EU Code User. The Company to provide handset only. | Control Telephony provides secure point to point telephony for routine Control Calls, priority Control Calls and emergency Control Calls. The Company will provide the communication routes and Control Telephony facilities to the EU Code User’s Control point. Any subsequent relocation of Control Point (within GB) will be charged to the EU Code User by The Company. |
| PSTN (or other off-site communications circuits) for Telephony. (ECC.6.5.2 to ECC.6.5.5 and ECC.7.9, OC.7 and BC.2) | Trading Point, Control Point | Public Telephone Operator (PTO). | Wiring to the Public Telecommunications Exchange including handset to be provided by The EU Code User. | Data and speech services required by The Company shall be cabled from the EU Code User site to the Public Telecommunications Exchange. The EU Code User shall only use the PSTN facilities for voice communications with The Company as detailed in ECC.6.5.4.5 and ECC.6.5.5.2 of the Grid Code. The EU Code User’s control point must be immediately and directly contactable by The Company at all times and operators should be able to communicate in clear plain English. |
| Trading Point Data Transfer (EDT) (ECC.6.5.8(a) and BC.1.4.1) | Trading Point | The Company Substation Exchange | EU Code User to provide and install EDT terminal. The EU Code User to provide communications path to the EDT terminal in conjunction with The Company in order to submit the data required by the Grid Code. | The Company to include site in instructor database and commission. Facility provided via Control Telephone and/or Facsimile machine. The EU Code User will provide the communications path for the EDT terminal from the EU Code User’s Trading Point and can elect to send this to two locations (Warwick or Wokingham). The Company will provide the necessary connection and interfacing equipment at both locations. If the EU Code User intends to have a nominated Trading Point outside Great Britain, the responsibilities, functionality, dependability, security, procurement, configuration, delivery points, protocol and repair times of the communication links to be agreed with The Company 6 months prior to Completion Date (Stage 1). |
| Data Entry Terminals (Electronic Despatch & Logging (EDL)) (ECC.6.5.8(b)) (Required only if the User is required to provide all Part 1 System Ancillary Services and wishes to participate in the Balancing Mechanism) | Control Point | Public Telephone Operator | EU Code User to provide and install EDL terminal approved by The Company which will permit submission and acceptance of Grid Code data between the EU Code User’s Control Point and The Company continuously. The Company to provide communications path to the EDL terminal (Great Britain only) in conjunction with the EU Code User. | The Company will provide the communication routes and Control Point Electronic Dispatch and Logging facilities to the EU Code User’s Control point. Any subsequent relocation of Control Point (within GB) will be charged to the EU Code User by The Company. |
| Designated Information Exchange System (ECC.6.5.9) | Trading Point and Control Point | Public Telephone Operator. | EU Code User to provide and install designated information exchange system and wiring to PTO. |  |

Note: The specifications for Control Telephony, EDT and EDL are defined in the Annex to the General Conditions of the Grid Code which is available on The Company’s website.  Please see reference to Electrical Standards on the Useful Links page at the end of this Appendix.

Note:

Before approval of GC0182

Grid Code Modification GC0182 is currently underway to formalise the requirements for GB Code Users and EU Code Users to follow a unified metering polarity convention when submitting power flow data to The Company. If GC0182 is approved by the Authority, the operational metering signals of GB Code Users and EU Code Users being installed or upgraded after a specific date, will need to adhere to the polarity convention as requested.

A guidance note has been published on The Company website highlighting the key principles of the proposed metering polarity convention. Please note that the key principles of the metering polarity convention are not mandatory. In the event that the Authority approve Grid Code Modification GC0182, it is proposed that the metering polarity convention will be developed into an Electrical Standard which would be applicable to those parties caught by the obligations of GC0182.

USEFUL LINKS

The Grid Code:

https://www.neso.energy/industry-information/codes/grid-code-gc

Electrical Standards:

Electrical standards documents | National Energy System Operator

Extranet (ID and password required, email transmission.documentcontrol@nationalgrid.com to request access):

Connection Policies and Guidance:

Connections | National Energy System Operator

Procurement Guidelines and Balancing Principles:

https://www.neso.energy/industry-information/codes/balancing-settlement-code-bsc/c9-statements-and-consultations