OPERATING CODE NO. 3

(OC3)

SYSTEM INCIDENTS REPORT

CONTENTS

(This contents page does not form part of the Grid Code)

Paragraph No/Title	Page Number

OC3.1   INTRODUCTION	2

OC3.2   OBJECTIVE	2

OC3.3   SCOPE	2

OC3.4   SYSTEM INCIDENTS REPORT	2

OC3.5   REPORTING ON FAULT EVENTS ………………………………………………………………….3

OC3.6   REPORTING ON LEARNING…………………………………………………………………………3

OC3.1	INTRODUCTION

OC3.1.1	Operating Code No.3 ("OC3") is concerned with the monthly publication by The Company of an incident report and Frequency data for the National Electricity Transmission System.

OC3.2	OBJECTIVE

OC3.2.1	The objective of OC3 is for The Company to produce a monthly report of incidents and frequency data. The report and data are important to industry and the Grid Code Review Panel as they help monitor the effectiveness of the technical requirements in the Grid Code and Distribution Code.

OC3.3	SCOPE

OC3 applies to The Company.

OC3.4	SYSTEM INCIDENTS REPORT

OC3.4.1	The Company shall publish monthly on the Website a report titled the System Incidents Report, which shall contain:

- a record of each and all of any of the following Events, defined as Significant Events, on the National Electricity Transmission System:

- an unplanned loss of infeed or exfeed (import or export including generation, Demand and interconnection) of =>250MW;

- a Frequency excursion outside the limits 49.7-50.3Hz;

- a fault on the National Electricity Transmission System which:

A.  could be linked to the known or reported unplanned tripping of 250MW or more as reported in (i) above; and/or

B. (as detailed in section CC6.1.4) is linked to a change in the Transmission System voltage of

I. 300kV or greater: > +/-5% for >15min; or

II. 132kV up to 300kV: > +/- 10% for >15min;

- any known demand disconnected >=50MW from the National Electricity Transmission System or other lesser demand if notified to The Company; and

- any Demand Control action taken;

- a report of each such Significant Event including the following data in relation to each Significant Event as appropriate and available:

- the time(s) in hh.mm.ss.mmm of the Significant Event and any potentially related occurrences;

- any known or reported loss of Embedded Power Station(s) with locations and ratings where available;

- the Frequency record from at least five (or seven where possible) System Restoration Regions (in table and graphical format) at <=100 millisecond intervals for 30 seconds before, up to one of the following:

  - 30 seconds after the Significant Event, or;

  - the duration until the Frequency recovers within the operational limits, or to the nominal frequency

- the Frequency (to 2 decimal places) immediately before the Significant Event;

- the Frequency (to 2 decimal places) immediately after the Significant Event;

- the maximum rate of change of Frequency recorded during the Significant Event over a specified time period of 500ms over a sliding 100ms window;

- where known, the MW of all individual losses or trips related to the Significant Event;

- where known, the identity of the Users and Network Operator of all demand losses or trips related to the Significant Event;

- the location of any reported Transmission fault on the network diagram and geographically;

- the extent of any voltage dip associated with the Significant Event;

- an estimate of system inertia in MWs at the time of the Significant Event along with how it has been calculated; and

- any other data available that is of value to gain a clearer understanding of the Significant Event and its potential implications; and

- a report on known events and associated data (including event times in hh.mm.ss.mmm) on the National Electricity Transmission System including:

- three phase faults;

- three phase to earth faults;

- phase to phase faults;

- phase to earth faults;

- the associated voltage dips – durations and spreads;

- over-voltages;

- under-voltages;

- voltage dips of >50%; and

- lightning strikes.

OC3.4.2	To obtain, manage, present, communicate and report the data in OC3.4.1 The Company shall:

(a)	present the System Incidents Report and provide associated data in spreadsheet or other downloadable format in The Company’s reasonable opinion;

(b)	maintain an area of the Website with a list of all historic System Incidents Reports and information on any process required for legitimate parties to obtain the reports (if reports are not available to download); and

(c)	notify all Electricity Distribution Licence holders and Network Operators at least monthly of every Significant Event and request information to fulfil its duties in OC3.4.1.

OC3.4.3	The Company shall prepare and publish the System Incidents Report monthly in accordance with the following timescales:

(a)	a data cut-off date of the end of each month for that reporting month;

(b) 	data to be collated, reviewed and processed in the subsequent  month for a reporting month;

(c)   System Incidents Report to be published at latest on the last working day of the first month after each reporting month (in other words the report for January would be published on the last working day of February, and so on) and published on the Website. For the avoidance of doubt, if there are no incidents arising under OC3.4.1 (a) - (c) a System Incidents Report would, nevertheless, still be published stating that ‘No System Incident occurred in month [X]’.

OC3.4.4	The Company shall publishon the Website, in a spreadsheet

or other appropriate downloadable format, continuous System Frequency data at a maximum of 100ms intervals with frequency measured at one or multiple locations (Historic Frequency Data)

and publish this on the Website, no later than the eleventh working day after the end of the reporting month.

OC3.5 	REPORTING ON FAULT EVENTS

OC.3.5.1 	The Company shall prepare and publish on their Website a report giving date, times (hh.mm.ss) that the fault was reported (noting this may be some seconds after the fault occurred) location of actual three phase, three phase to earth, phase to phase and phase to earth fault events on the National Electricity Transmission System.  Information shall be published as soon as reasonably practicable following such an event.  For faults in which a fault ride through issue was found,  appropriate waveform information will be provided if available.

OC3.6	ANNUAL REPORTING

OC3.6.1	Using best endeavours, The Company shall produce an annual report at latest by 30 September following the end of the 12-month reporting period. This Annual System Incidents Report shall:

- review and examine all the data in the previous 12 months of System Incidents Reports;

- compare trends to previous 12-month periods;

- highlight the most Significant Events and learnings from these;

- look for any trends or emerging issues for the System;

- publish analysis of frequency duration data and trends;

- provide updates on new or improved measurements and data collection and analysis on the System;

- request feedback from industry on analysis, learnings and trends.

The Company shall and present the Annual System Incidents Report to the Grid Code Review Panel and publish the report on the Website inviting comments for improvements and omissions which shall be considered and addressed in the following Annual System Incidents Report.

< END OF OPERATING CODE NO. 3 >